## Appendix D Outline
Appendix D Checklist when selecting a facility location
Applicable Section in Chapter 4 |  | Worksheet
Issued 06-April-2018
4.2 | Additional Information on the Facility | Table D.1 Checklist for Initial Evaluation and Location Selection
4.3 | Selecting a Team to Locate the Facility
4.5 | Determining the Location Plot Size
4.6 | Construction and Turnaround Issues
4.7 | Maps and Information
4.8 | Geological Issues | Table D.2 Checklist for Location Characteristics
4.9 | Weather Issues
4.1 | Seismic Issues
4.11 | Off-site Issues | Table D.3 Checklist for Off-site Interface
4.12 | Security Issues
4.13 | Environmental Issues | Table D.4 Checklist for Environmental Concerns
4.14 | Infrastructure Issues | Table D.5 Checklist for Infrastructure and Building Concerns
4.15 | Building and Structure Issues
4.16 | Material Handling Issues | Table D.6 Checklist for Material Handling Concerns
4.17 | Communication Issues | Table D.7 Checklist for Communication and Design Issues
4.18 | Engineering Design Issues
4.19 | Utilities Issues | Table D.8 Checklist for Utilities Concerns
4.2 | Other Characteristics | Table D.9 Checklist for Other Concerns
Note: This list is not all inclusive. Please share any proposed additions/corrections by sending them to the CCPS. Thank you, in advance, for sharing your insights and experiences.

## Appendix D - Table D.1
Appendix D - Table D.1 - Checklist for Initial Evaluation and Location Selection
Issued 06-April-2018
Line Item | Section in Chapter 4 |  | Details or n/a | Action? (Yes/No)
1 | 4.2 | Additional Information on the Facility
2 |  | Who and where are key customers for the products?
3 |  | Who and where are the key suppliers for feedstocks?
4 |  | Provide a description of how feedstocks and products will be transported into, within, and from the facility (e.g., truck, rail, ship, pipeline, by company owned means or contract), including the expected cargo sizes and frequencies of shipments into and out of the facility.
5 |  | Will the new/expanded asset be self sustaining or will import/export to third parties be required?
6 |  | Provide a description of the turnaround philosophy (e.g., shuts down once every two years, or continued operation with individual process shutdowns as required).
7 |  | Provide a description of the expected life of the process unit (e.g., 10 years, 20 years, etc.), including the desired operations utilization or on-stream factor.
8 |  | Could the new expansion or location and its equipment be used for a new process involving different chemicals and reactions?
9 |  | What is the planned level of staffing for operation and maintenance of the site?
10 |  | Are specialized outsourced maintenance and/or inspection skills required?
11 |  | If the location is within a complex, are there activities at neighboring facilities that may impact on the expansion project or new facility?
12 |  | Is there experience at other similar facilities with community concerns or productivity issues (e.g., noise, odors, traffic issues, or high personnel turnover). | Noise: See Questions in Table D.4, Section 4.13.6
13 |  | Should the location selection team anticipate additional land for future expansions or facilities?
14 |  | Is there the for community concerns regarding location development or expansion?
15 |  | Is the facility going to be built on a “greenfield” site, a “brownfield” site, or an existing site, or land that has been previously used, abandoned, and now awaits a new use?
16 |  | Consider for brownfields: due diligence and remaining service life assessment for existing facilities/jetties/docks.
17 |  | Consider for brownfields: due diligence and remaining service life assessment for existing facilities that will be taken over, or connected with new facility/jetty/dock.
18 |  | If the new plant is to be built on an existing site, what field data may already be available to reduce the data collection effort?
19 |  | What types of facilities/operations have occupied the location?
20 |  | Are there any live or abandoned pipelines and /or live or abandoned utilities crossing the site or at site boundary?
21 |  | Survey site to ensure site is clear for ground preparation (civil works) without potential, associated re-routing costs.
22 |  | Do existing pipelines transport materials over public or private land or rail links?
23 |  | Is there a risk of land mines or unexploded munitions from past military conflicts?
24 |  | Is there land surrounding the site to allow purchase of, or control of, that land to provide a buffer zone (i.e., to prevent future population encroachment)?
25 |  | Is there secure access or is access via rights-of-way and land of others parties?
26 |  | Are there any specific zoning restrictions surrounding the location?
27 | 4.3 | Selecting a Team to Locate the Facility
28 |  | List of member(s) with knowledge of the types of process unit and processes under consideration for the new facility.
29 |  | List of member(s) with knowledge of the company's policies and guidelines, including the level of analyses required, when locating or expanding facilities (e.g., performing quantified dispersion analyses before selecting a location).
30 |  | List of member(s) with knowledge of facility process unit and/or equipment layout distances.
31 |  | List of member(s) with knowledge of the specific geographic areas where the new facility is planned or being considered.
32 |  | List of member(s) with familiarity and /or expertise with the local language.
33 |  | List of member(s) with familiarity and /or expertise with the local regulations.
34 |  | Process safety and risk specialist who can evaluate the on-site and off-site process safety issues (refer to Chapter 3).
35 |  | Environmental specialist who can evaluate the facility’s wastewater, ground water, and air issues.
36 |  | Civil engineering specialist who can evaluate the topography and soil conditions for the facility.
37 |  | Security specialist who can assist evaluate physical security considerations (including transportation of workers and materials during turnarounds/construction). | Note: For U.S. facilities, the Department of Homeland Security (DHS) standards must be addressed.
38 |  | Transportation specialist who can evaluate specific issues for facility access by rail, truck, barge, Very Large Cargo Carrier (VLCC) crude tankers, iso containers, etc., and who can evaluate specific issues for transportation of hazardous materials within the facility.
39 |  | Pipeline specialist who can evaluate specific issues for materials being conveyed through overhead or underground pipelines.
40 | 4.5 | Determining the Location Plot Size
41 |  | What are the plot dimensions expected for the facility location?
42 |  | Are off-site risks addressed in the amount of land needed? | Refer to Appendix C
43 |  | Is the location plot size and surrounding area suitable for a future expansion?
44 |  | Determine the cost for land required for the facility and rights-of-ways. Describe rights-of-ways that are required.
45 |  | Besides land for facility location itself, consider land availability locally for the laydown, warehousing, and construction camp.
46 | 4.6 | Construction and Turnaround Issues | Also noted for awareness in Appendix E, Chapter 5, Section 5.6 (See Questions in Table D.5, Section 4.14)
47 |  | Consider parallel projects and possible disturbances/strikes by neighbor or construction workforces.
48 |  | How will construction staff, operations and maintenance arrive to site? | Consider secure transport arrangements and parking.
49 |  | How much security is needed for the construction camp and of procured items on route to site, etc.? | Consider secure transport arrangements.
50 |  | Are there any anticipated environmental permitting concerns when constructing the facility?
51 |  | Are there any anticipated permitting concerns related to the facility construction and/or operation.
52 |  | Determine the quality of the groundwater (salt or fresh), contaminants (i.e., high sulphates that can affect cement foundations), and the pH value.
53 |  | Are there any special groundwater monitoring, groundwater protection (i.e., dikes or spillways for hydrocarbon releases, etc.), or groundwater drainage issues?
54 |  | Are construction jetties/docks available for ship delivery?
55 |  | Are there adequate construction transportation routes to facility's location?
56 |  | Is a heavy haul road available for bringing in the largest vessels or skids from the point of manufacture to the site?
57 |  | Are bridge weight limits on the route acceptable (transport over the bridge)?
58 |  | Are bridge height limits sufficient (transport under the bridge)?
59 |  | Are water unloading facilities sufficient (wharf unloading) and pier crane placements?
60 |  | Are public interstate interchanges or a railway bridge overpasses available or needed?
61 | 4.7 | Maps and Information
62 |  | Obtain a topographical map of the proposed area (with contours including elevations above sea level). | Note: In general, either 1 to 2 ft. or 25 to 50 cm contours provide good definition.
63 |  | Obtain a general map of the area showing boundaries of the proposed location (in relation to true north and magnetic north).
64 |  | Obtain a general map of the geographic area (includes steep slopes, forests, swamps, rocky terrain and natural drainage conditions).
65 |  | Obtain aerial and ground photographs of the entire location. The ground photographs should be made from two or three directions to define the location.
66 |  | Are there adjacent process units or facilities, structures, jetties/docks, and roads?
67 |  | Do the adjacent or nearby process units or facilities have associated hazards (e.g., materials, processes, terminals, or other jetties/docks).
68 |  | If the new Process Unit is to be located within an existing complex, procure all pertinent and available drawings of the existing processes and buildings.
69 |  | Is there land available for future expansion?
70 |  | Obtain a map of the harbor showing harbor boundaries, pier head lines, channels, soundings, and river velocity.
71 |  | If applicable, identify the following areas on the land surrounding the location under consideration:
72 |  | Environmentally sensitive areas, such as wetlands, wildlife, and fauna
73 |  | Residential areas
74 |  | Schools
75 |  | Day care centers
76 |  | Nursing homes
77 |  | Hospitals
78 |  | Prisons
79 |  | Farms and agricultural centers
80 |  | Resorts
81 |  | Business areas, town centers, malls and shopping centers
82 |  | Industrial, manufacturing, or warehouse areas
83 |  | Estimated day-time and night-time populations of surrounding communities/industries
84 |  | short-term, high population meeting/gathering areas for the community (e.g., concerts, religious events).
85 |  | Public parks
86 |  | National treasures or landmarks
87 |  | Historically or archeologically sensitive areas
88 |  | Cemeteries, knowledge of burial lands
89 |  | Airports
90 |  | Points of national interest such as nuclear power plants, military bases, or major historical sites
91 |  | Utility rights-of-way and easements and any planned upgrades
92 |  | Sewers, water mains, and storm drainage
93 |  | Natural gas and other pipelines
94 |  | Planned road widening or upgrades including any bridge upgrades or replacements
95 |  | Radio, television, or microwave communication services that may be subject to interference from a new facility or may interfere with the communication or operation of the facility

## Appendix D - Table D.2
Appendix D - Table D.2 - Checklist for Location Characteristics
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.8 | Geological Issues
2 |  | 4.8.1 | Terrain properties
3 |  | 4.8.2 | Soil properties
4 |  |  | Determine if excavation will require sheet pilings or well point systems. Local contractors or inspectors may have information regarding how excavation work is presently performed in the area.
5 |  |  | If available, acquire information regarding the for in-ground corrosion of pipes and foundations. Data may be available from local contractors, local industry, or land survey companies regarding: | Including: The USGS (United States Geological Survey) www.usgs.gov
6 |  |  | Is there for stray electrical ground currents produced up to 20 miles (30 km) away? | Example: The electrical current from electrified railways that could cause electrolytic corrosion of buried steel pipe or support piles.
7 |  |  | Is there experience using cathodic protection in the area around or on the new facility?
8 |  |  | Obtain soil data on nearby locations, if available. Soil stability information is needed for locations with hills or steep slopes.
9 |  |  | Obtain information for:
10 |  |  | Earthquakes | See Questions in Section 10.4 - Seismic Issues.
11 |  |  | Landslides
12 |  |  | Sinkholes
13 |  |  | Soil liquefaction (quicksand)
14 |  |  | Debris flows and rockfalls.
15 |  |  | Rockfalls
16 |  |  | Obtain data on nearby heavy structures regarding loading, type of foundations, settlement, etc., if available.
17 |  |  | Determine if the location’s natural soil has sufficient load bearing capacity to support heavy construction equipment. If not, then determine what type of compacted fill or sand will be required to prepare the location for construction. Obtain the opinion of local contractors in this regard if possible.
18 |  |  | Once the location has been chosen, a follow-up soils investigation will be required. The survey team should determine if reports on soil conditions are available for the location being surveyed through local contractors or land survey offices. Specific information to look for includes borings and soil bearing tests.
19 |  |  | Investigate soil properties to anticipate the need for contaminant remediation.
20 |  |  | Determine the type of vegetation and precautions necessary to prevent soil erosion.
21 |  |  | Determine if there is a suitable area where soil can be discarded.
22 |  |  | Determine if dredging or fill will be required.
23 |  |  | Determine if bulkheads will be required to prevent soil slumping and what the estimated dimensions will be (How long? How high?)
24 |  |  | Are tunnels, mine shafts, or injection wells present?
25 |  |  | Determine the depth to the frost line (if any). Frost penetration data will be needed to determine minimum foundation depths and underground piping designs. Also determine the dates for earliest and latest frost recorded.
26 |  |  | Are there other natural hazards that need to be considered?
27 |  |  | Natural underground caverns
28 |  |  | Large tidal swings
29 |  |  | Salty coastal air
30 |  |  | Tsunami
31 |  |  | Volcano | Consider also ash loadings for roof and building designs, HVAC air filters, etc.
32 | 4.9 | Weather Issues |  | (i.e., climate conditions)
33 |  |  | Temperature conditions for the facility. These in include:
34 |  |  | Annual Average Temperature (used in air cooler design and insulation thickness calculations)
35 |  |  | Coldest Month Average Temperature (used in heating design work)
36 |  |  | Lowest One-Day Mean Temperature (used in calculating minimum metal design temperatures for pressurized equipment)
37 |  |  | Extreme Low Temperature (used in design of weather protection requirements)
38 |  |  | Heating and Cooling Criteria (Summer Wet Bulb and Dry Bulb Temperatures, and Winter Dry Bulb Temperature)
39 |  |  | Humidity conditions for the location. Gather the average readings for each month.
40 |  |  | Wind Conditions from local weather stations that include the following data:
41 |  |  | Basic Wind Speed (used for design of structures, buildings, pressure vessels, piping, storage tanks, air coolers, cooling towers, and stacks).
42 |  |  | Mean Wind Velocity (used for air pollution calculations, stack considerations, and insulation thickness requirements)
43 |  |  | Prevailing Wind Direction – generally in the form of a wind rose indicating the percent of time the wind blows in 16 radial directions (N, NNE, NE, ENE, E, etc.; see Chapter 3, Figure 3.1 for additional discussion on the wind rose). An analysis by season is most useful.
44 |  |  | Precipitation categories, including:
45 |  |  | Rainfall, usually given as 10-year average and maximums for one month, 24 hours, one hour and 30 minutes
46 |  |  | Maximum Snow Load based on local code design requirements (used in building roof designs, structural platform design, and storage tank designs)
47 |  |  | Ice load, if available, can be useful in design of structures and buildings.
48 |  |  | Severe weather conditions by season (also noted by insurance companies as “Natural Perils”) that may cause interruption of facility operations, include the following:
49 |  |  | Is area subject to fog? If so, what are the frequency and intensity of fog alerts?
50 |  |  | Tornados - frequency and worst-case recorded severity.
51 |  |  | Hurricanes or typhoons - frequency and historic worst-case scenarios (maximum winds and rainfall).
52 |  |  | Floods - including dates, total rainfall, and flood depth at the facility as well as access road low points and at planned marine operation locations. | Note: If local roads are subject to flooding, consider alternate routes to reduce logistics and personnel accessibility disruptions.
53 |  |  | If there is a flood control organization for the area, determine who is responsible for maintenance and operation of the flood control equipment (locks, pumps, and levee).
54 |  |  | Has there been a flood model developed for the area and has it been validated? | See Table D.6, Section 4.16.6, under Marine Regulations, for a rare “navigable waters” issue in the United States regarding an area’s “flash flood” potential.
55 |  |  | Is the area protected from flood by a levee?
56 |  |  | If so, who maintains the levee and controls access to the navigable waterway?
57 |  |  | Drought - recorded history should be collected to determine the water availability during a drought and impact on the area from the facility in a drought situation.
58 |  |  | Dust Storm - activity, frequency, and records of previous storms.
59 |  |  | Icing and heavy snows - annual snow falls.
60 |  |  | Lightning strike frequency - used when designing lightning protection for processing and storage tank operations.
61 |  |  | Does a high likelihood for lightning strikes delay essential outdoor operations?
62 | 4.1 | Seismic Issues
63 |  |  | What is the earthquake zone for the area?
64 |  |  | Are there active fault lines in the area?
65 |  |  | Is the area subject to earthquakes? If so, what design and seismic coefficient is used by local authorities or structural engineers?

## Appendix D - Table D.3
Appendix D - Table D.3 - Checklist for Off-site Interface
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.11 | Off-site Issues
2 |  | 4.11.1 | Neighboring forests and vegetation
3 |  |  | Is the area surrounded by forests?
4 |  |  | If so, do the trees and vegetation contribute to congestion and obstruction, such that they increase the for a vapor cloud explosion (VCE) blast overpressure?
5 |  |  | If so, will the vegetation surrounding the facility be killed or contaminated if exposed to a released material?
6 |  | 4.11.2 | Neighboring industrial facilities
7 |  |  | Is the area surrounded by other industrial facilities?
8 |  |  | If so, can hazards from the new location impact the neighbors?
9 |  |  | If so, can hazards from a neighboring facility impact the new location?
10 |  |  | Consider an “overall” risk profile for all facilities in the complex.
11 |  | 4.11.3 | External emergency response resources
12 |  |  | What emergency response accessibility issues should be considered?
13 |  |  | Describe local firefighting operations. Obtain drawings of nearest municipal fire mains showing size, capacity, and pressure. Indicate the location of fire stations relative to the facility.
14 |  |  | What regulations govern the provision of firefighting equipment for tankage or process units and other fire and safety operations?
15 |  |  | What emergency services are available in the area?
16 |  |  | Burn Center (yes/no)
17 |  |  | Medical Clinic (yes/no)
18 |  |  | Ambulance (yes/no)
19 |  |  | Airlift to major medical centers (yes/no)
20 |  |  | Fire departments (yes/no)
21 |  |  | Facility fire brigade (yes/no)
22 |  |  | Area mutual aid (yes/no) | See Question 38 below: Will mutual aid providers be needed?
23 |  |  | Consider capabilities for fire trucks, fire fighters, and other equipment from surrounding areas, such as:
24 |  |  | City (yes/no)
25 |  |  | Volunteer (yes/no)
26 |  |  | What is response time for local or distance medical response and fire responders?
27 |  |  | Is there emergency response for remote locations (e.g., marine jetties/docks)?
28 |  |  | Describe onshore response and offshore responses for terminal, jetty/dock emergencies. | Consider river, canal or seaborne fire fighting boats for jetty/dock fires, etc.
29 |  |  | What is the quality of the emergency services?
30 |  |  | Are shared emergency services available from the complex or adjacent facilities?
31 |  |  | If so, what shared service emergency equipment is available to help manage facility specific hazards? (e.g., ladder fire trucks, pumper fire trucks, foam supplies, foam monitors, etc.)
32 |  |  | Does the road structure permit good emergency access to the facility?
33 |  |  | Is timely response an issue (i.e., are responders nearby)? (yes/no)
34 |  |  | If not, how will responses to pool fires, jet fires, etc.be handled?
35 |  |  | What other emergency responses and evacuations must be considered? (i.e., bomb threats, etc.)
36 |  |  | What are the plans for internal and external emergency response capabilities (if any)
37 |  |  | Will incidents impact the facility such that the facility will need additional fire and emergency medical services from surrounding community resources? | (Note that greater distances from these resources will increase the effective emergency response time.)
38 |  |  | If so, identify the existing “mutual aid” responders.
39 |  |  | Identify if they are needed for direct response
40 |  |  | Identify if they are needed in addition to the facility’s ERT
41 |  |  | Identify facility resources who will establish the community emergency response planning and drills.
42 |  | 4.11.4 | Stakeholder Outreach
43 |  |  | Are there any stakeholder outreach groups that exist or need to be established? (i.e., CAP - Community Action Panels, LEPC - Local Emergency Planning Committee)
44 | 4.12 | Security Issues
45 |  |  | What local/nearby police, levee patrol or coast guard protection resources are available in the surrounding area, including at the facility fence line, at the jetties/docks, for rail and for pipeline?
46 |  |  | Are any plot perimeter walling is required for security reasons?
47 |  |  | Does the country have a history of business kidnapping for corporate ransoms?
48 |  |  | Does the country have a history of imposing visa restrictions that would hinder the development or operation of the facility?
49 |  |  | Are there special security measures that must be addressed? | Note: Consider if special security provisions are needed for workers and materials during turnarounds/construction.
50 |  |  | Note: United States locations with waterway docks fall under Coast Guard maritime security measures known as MARSEC. MARSEC levels (1, 2, and 3) will impact access into a facility for everyone (logistics, police, state and federal personnel). A Transportation Worker Identification Credential (TWIC) card is required for normal access and requires 6-8 weeks for a United States governmental background check. In applicable, these facilities must consider construction access and on-site TWIC applications and verifications, as well.
51 |  |  | Is there the for hunter or chased wildlife intrusion during the hunting season?
52 |  |  | Are there other wildlife intrusion concerns? (including Pigeons, birds, snakes, rodents, deer, stray farm animals)
53 |  |  | Are there specific chemicals that are illegal drug precursors?
54 |  |  | Are there specific chemicals for weapons or weapons precursors?
55 |  |  | What security accessibility issues should be considered?
56 |  |  | To what extent can the local police or shared facility security be used on a construction project and when the facility is operational?
57 |  |  | Are fences and additional guards needed at the facility?
58 |  |  | Are there posted signs and locks on fence gates?
59 |  |  | Is video surveillance available and/or needed?
60 |  |  | Is there a history of theft or vandalism at other facilities in the area?
61 |  |  | Is the area’s political environment aligned with the company's values?
62 |  |  | Will a political shift or change in leadership have an impact on facility ownership or manufacturing ability? | (For example, is there a possibility of future trade sanctions which may be imposed by an unfriendly government?)
63 |  |  | Is there for violent demonstrations, sabotage, or terrorism?

## Appendix D - Table D.4
Appendix D - Table D.4 - Checklist for Environmental Concerns
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.13 | Environmental Issues
2 |  | 4.13.1 | Environmental impact assessments (EIA)
3 |  |  | Is an environmental impact assessment/statement required? If so, specific information acquired during the location survey may help focus the issues of concern.
4 |  |  | Are other EIAs available (typically requires 2 seasons data)?
5 |  | 4.13.2 | Environmental regulations
6 |  |  | Are there any construction-related permitting concerns or environmental issues?
7 |  |  | Are any landscaping or green areas are needed as part of site development? | These may be required (as % of overall plot plan) or requested at or near facility boundary to secure fence and screen facilities from roads or public. (Note: Green tree/bush plantings can be in conflict with Buncefield conclusions.)
8 |  |  | What are the regulations regarding storm water discharge without treatment?
9 |  |  | Are there any environmental permitting concerns when operating the facility?
10 |  |  | What do the regulations specify regarding the level of treatment required for industrial wastewater?
11 |  |  | What are the performance requirements for the waste treatment facility? Is there a requirement to submit treatment facility operating reports? What data needs to be reported?
12 |  |  | Do the regulations specifying analytical methods to be used in determining the level of specific impurities in the effluent include hydrocarbon or toxic materials content? This is an operating cost issue.
13 |  |  | Are there any regulatory issues associated with the chemicals?
14 |  |  | Are there any requirements for waste disposal? (See hazardous waste issues below)
15 |  |  | Do local waste regulations require zero liquid discharge (ZLD)? | Note: If so, then complicated waste water recycle/treatment/evaporation systems may be required.
16 |  |  | Are there any regulatory restrictions on dusts or on location of dust generating facilities? | Note: May have mandatory minimum distances from facility boundaries. Applicable to coke, coal and power stations.
17 |  | 4.13.3 | Air issues
18 |  |  | Are there any special topographical characteristics such as nearby hills or valleys that can affect dispersal of air pollutants?
19 |  |  | What are the requirements for vapor recovery in tank truck, rail car or marine loading operations? | For example: Will geodesic domes or vapor recovery systems be needed for emissions control from storage tanks?
20 |  |  | Consider truck top/bottom loading and unloading transfers. | For example: truck gantry/loading arm or hose been evaluated for deflagration/explosion studies.
21 |  |  | Consider marine facility ship to shore/shore to ship and rail car transfers. | For example: loading arm or hose been evaluated for deflagration/explosion studies.
22 |  |  | Is a standby supply of low-sulfur fuel required should an air pollutant alert or emergency occur?
23 |  |  | What are the national, state, and local regulations in effect for discharge of sulfur oxides, particulate matter, carbon monoxide, photochemical oxidants, hydrocarbons, nitrogen dioxide, other applicable chemicals, and odors?
24 |  |  | Obtain a copy of relevant regulations with the latest addenda, if available.
25 |  |  | If a copy of these regulations cannot be obtained, the following questions should be answered.
26 |  |  | What are permissible limits of pollutants such as CO, CO2, sulfur dioxide, solids, smoke, and others that can be discharged to the atmosphere?
27 |  |  | What control, if any, governs the height of industrial stacks?
28 |  |  | What is the average height of industrial stacks in the general vicinity?
29 |  |  | Must plans for air control systems be submitted to control authorities for approval?
30 |  |  | What penalties are included in the regulations, how are they assessed, and what legal recourse does the accused have?
31 |  |  | What is the process for, and time required, to obtain a waiver or exception?
32 |  |  | Are operating permits required to run air quality control equipment?
33 |  |  | What agencies enforce regulations? Outline their organizations. How is the law enforced? What are the powers of control officers? Where air quality is not regulated by the central government, to what extent does the local government control emissions?
34 |  |  | In the event that air contamination is not controlled by definitive measures enforced by an official body, is there any governmental control, local or otherwise, and to what extent?
35 |  |  | What is the general governmental expectations/requirements regarding air contamination control?
36 |  |  | What is the working relationship with the regulatory, local or corporate control officials?
37 |  |  | Is there any indication that existing regulations will be tightened or new regulations adopted where none exist at the moment?
38 |  |  | What is the perception of the general public toward air contamination as reflected by civic groups and newspaper publicity?
39 |  |  | Do any technical groups exist that monitor air contamination control?
40 |  |  | What is the nature of industrial emissions to the atmosphere near the facility?
41 |  |  | Obtain data on existing levels of atmospheric pollutants such as sulfur dioxide, dust falls, hydrogen sulfide, and smoke. Odor should be included.
42 |  |  | Is local industry organized into a group for exchange of information on air contamination and air quality control? | Example: Concentration of dust particles: _________ ppm (normal); _________ ppm (maximum).
43 |  | 4.13.4 | Land issues (hazardous waste control)
44 |  |  | What governmental regulation is in effect that must be applied to hazardous wastes?
45 |  |  | Obtain copies of regulations that apply to hazardous wastes.
46 |  |  | Determine how the facility will manage its hazardous wastes, includes temporary on-site storage, packaging, transportation, and ultimate disposal (e.g., secure landfill or incineration). | Responsibilities for on-site management, transporting and disposal of hazardous wastes must be clearly identified.
47 |  |  | Consider availability of off-site hazardous waste disposal sites, specific cargo route limitations, and distances from facility location.
48 |  | 4.13.5 | Water issues
49 |  |  | Wastewater Quality Control
50 |  |  | What governmental regulation is in effect that must be applied to industrial wastes and the quality of the effluent discharged into natural water bodies?
51 |  |  | What governmental regulation is in effect that must be applied to sanitary sewage and the quality of the effluent discharged into natural water bodies?
52 |  |  | Obtain copies of regulations that apply to both industrial wastes and sanitary sewage. In addition, obtain copies of approved designs of sanitary sewage treatment systems.
53 |  |  | Identify means of disposing of facility effluent: dirty process water, sanitary sewage, and storm water.
54 |  |  | Consider the level of contamination and that the source of cooling waters should not be affected by the facility effluent.
55 |  |  | Furnish data giving pertinent information regarding local and state regulations for all types of buildings regarding sanitary and plumbing requirements.
56 |  |  | If such copies cannot be obtained, the following information should be sought from proper sources.
57 |  |  | What degree of treatment is specified for sanitary sewage?
58 |  |  | What quality standards are imposed on sanitary sewage and industrial wastewater effluents?
59 |  |  | Will septic tanks be permitted for remote areas, for a small number of occupants? Is there a point where septic tanks are not permitted and other, more expensive methods of disposal required?
60 |  |  | What agency enforces the regulations and what is the organization of the agency?
61 |  |  | In the event that waste discharge is not controlled by definitive legal measures enforced by an official body, is there any governmental control, local or otherwise, and what is the extent of this control?
62 |  |  | What is the general expectations/requirements regarding waste discharge control?
63 |  |  | What is the attitude of the regulatory, local or corporate control officials?
64 |  |  | Is there any indication that existing regulations will be tightened or new regulations adopted where none exist at the moment? If so, obtain a forecast or timetable for the new requirements
65 |  |  | What natural water body will receive the wastewater effluent from the new facility?
66 |  |  | Obtain quantitative and qualitative data on seasonal flow if discharge is to a stream.
67 |  |  | Obtain information on currents and tidal variations if discharge is to a lake or harbor.
68 |  |  | Are the natural receiving water bodies contaminated at present? If so, to what extent?
69 |  |  | Give locations of the following with respect to the facility:
70 |  |  | Commercial fishing areas
71 |  |  | Recreational areas for swimming, boating, or fishing
72 |  |  | Residential areas
73 |  |  | Domestic and industrial water supply intakes downstream of the proposed facility outfall
74 |  |  | Municipal sewage and industrial waste treatment operating outfalls both upstream and downstream of the proposed facility
75 |  |  | If available, provide analytical data (sufficient to show seasonal variation) on receiving water as listed:
76 |  |  | Temperature
77 |  |  | Turbidity
78 |  |  | Color
79 |  |  | Suspended solids
80 |  |  | Odor – concentration of concern
81 |  |  | Dissolved solids
82 |  |  | Dissolved oxygen
83 |  |  | Chemical and biochemical oxygen demand
84 |  |  | Total sulfur
85 |  |  | Oil content
86 |  |  | Phenol content
87 |  |  | Acidity, alkalinity, pH
88 |  |  | What is the attitude of the general public towards waste disposal control as reflected by civic group activity and newspaper publicity?
89 |  |  | Is local industry organized into a group for exchange of information on water contamination?
90 |  |  | Do any national technical groups exist that monitor water contamination control?
91 |  |  | Is it permissible to discharge clean storm water without treatment?
92 |  |  | What degree of treatment is specified for industrial wastewater?
93 |  |  | What water quality standards are imposed on industrial wastewater effluents? Are effective water standards controlled by receiving water quality or by discharge effluent quality?
94 |  |  | What requirements are there regarding submission of plans for treatment systems for approval of control authorities?
95 |  |  | What requirements are there for permits, and where are they obtained for operation of approved treating operations?
96 |  |  | What requirements are there for qualification by test of treatment plant performance?
97 |  |  | What requirements are there for submission of treatment system operating reports and what data are to be provided to authorities?
98 |  |  | Are there regulations specifying analytical methods to be used in determining the level of specific impurities in the effluent, including hydrocarbon or toxic materials content?
99 |  |  | Are penalties included in those regulations? If so, what is the method of assessment and what recourse is available to the owner or operator?
100 |  |  | Assess the impact from off-site water effluent by determining the following:
101 |  |  | Determine which natural body of water will receive the drainage and wastewater effluent from the facility.
102 |  |  | Can natural drainage from adjacent areas be diverted around the facility, or must it be treated as storm water entering the facility?
103 |  |  | What are the water quality criteria for the receiving water?
104 |  |  | In the case where receiving water is a stream, acquire quantitative and qualitative data on seasonal flow if available. The data should reflect seasonal variations in receiving water quality for all parameters used in evaluating effluent discharge quality.
105 |  |  | In the cases of lakes or harbors, information on currents and tidal variations or lake water elevations is desirable.
106 |  |  | Sanitary Sewage Collection and Treatment
107 |  |  | Obtain regulations regarding collection and treatment of sanitary sewage.
108 |  |  | Identify means of disposing of facility sanitary sewage.
109 |  |  | Could sanitary sewage from the new facility be discharged to municipal sewers?
110 |  |  | Could sludge from sanitary sewage treatment be disposed of through local companies?
111 |  |  | Describe existing sanitary sewerage and drainage systems in the area of the new facility. Provide the size of main pipelines and the proximity of main pipelines to the facility.
112 |  |  | If temporary sanitary sewer treatment is needed, what measures need to be taken? (Select the design rate for automatic or portable toilets based on current design standards.)
113 |  | 4.13.6 | Noise issues
114 |  |  | Determine if noise levels are regulated in the area. If so, collect data on the current noise levels for day and night levels.
115 |  |  | Determine local noise limits. | Notes: Industrial zones may have higher limits than zones for adjacent public communities. Noise limits are often lower at night. Construction and completions noise e.g., steam blowing needs to be considered as well as actual 24/7 operation.
116 |  | 4.13.7 | Luminosity issues
117 |  |  | Determine if luminosity levels are regulated in the area. If so, collect data on the current levels.
118 |  |  | Does the facility have hills or trees or other characteristics to block the light from the facility?
119 |  | 4.13.8 | Flare issues
120 |  |  | Are there restrictions for new flares?
121 |  |  | Some areas may restrict flaring, such as no new elevated flares (per public demand) or may have requirements for ground flares designed for less visible impact.
122 |  |  | Is there a height or zoning restriction for flares?
123 |  |  | Are their regulations that limit the flare exit velocity? (e.g., for pipe flares applied in the U.S. as control technology for volatile organic compound (VOC) emissions)
124 |  | 4.13.9 | Incinerator and boiler issues
125 |  |  | Are there any restrictions or permitting required for incinerators?
126 |  |  | Are there any restrictions or permitting required for boilers?
127 |  | 4.13.10 | Biological hazards
128 |  |  | Does the location have biological hazard considerations, such as the likelihood for any of the following:
129 |  |  | Wildlife, including poisonous snakes, bees, wasps, hornets, spiders, scorpions, fire ants, etc.
130 |  |  | Vegetation, including poison ivy
131 |  |  | Virus | (i.e., need to ensure or establish a prevention program for blood borne pathogens, especially critical for protection of emergency responders)
132 |  |  | Hepatitis | (i.e., need to ensure or establish a prevention program for workers assigned to work in with sanitary systems)
133 |  |  | Bacteria (e.g., cholera areas)
134 |  |  | Utilities water treatment facilities, for loss of the treatment medium (e.g., bacteria)

## Appendix D - Table D.5
Appendix D - Table D.5 - Checklist for Infrastructure and Building Concerns
Issued 06-April-2018
Line Item | Section in Chapter 4 |  | Details or n/a | Action? (Yes/No)
1 | 4.14 | Infrastructure Issues | (See Questions in Table D.1, Section 4.6) (See Questions in Table D.5, Section 4.16)
2 |  | What are the local air transportation service capabilities and how far are they from the location? If commercial service is available, are flights frequent or infrequent?
3 |  | What is the location's accessibility to marine ports or heliports?
4 |  | What public infrastructure is required (such as a highway interchange or a railway bridge overpass)?
5 |  | Are there infrastructure requirements for new or existing locations, such as:
6 |  | Road access for construction and ongoing operations?
7 |  | Alternate (second, separate) and secure access for security, fire authorities and/or emergency responders?
8 |  | Rail transportation facilities including rail car staging and storage capabilities?
9 |  | Port (marine) facilities for barges, coastal tankers and blue water vessels?
10 |  | Nearby airports with an adequate number of flights?
11 |  | Will the proposed location require, or benefit from, building a new airstrip and infrastructure?
12 |  | Electric power supply from the local utility and/or installed power generation facilities?
13 |  | Raw, process and potable water requirements?
14 |  | Fuel gas requirements?
15 |  | Nitrogen and other industrial gas requirements?
16 | 4.15 | Building and Structure Issues | See specific layout-related questions in Appendix E, Chapter 5, Section 5.13 See specific structure-related questions in Appendix F, Chapter 6, Section 6.6
17 |  | Consider safe and secure site and constructor parking. | For example: offsite, segregated parking for cars, motorcycles, cycles, etc.
18 |  | Consider inherently safe layout mini-study to minimize personnel/vehicle interactions.

## Appendix D - Table D.6
Appendix D - Table D.6 - Checklist for Material Handling Concerns
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.16 | Material handling issues
2 |  | 4.16.1 | Construction Transportation Issues
3 |  |  | Have transportation/infrastructure issues for construction been considered? | (See Questions in Table D.5, Section 4.14)
4 |  | 4.16.2 | Operations Transportation Issues
5 |  |  | Have transportation/infrastructure issues for operations been considered? | (See Questions in Table D.5, Section 4.14)
6 |  |  | Describe in detail the anticipated methods of bringing feedstock into the facility and distributing products from the facility. State the limitations regarding the number and grades of products that can be handled by ship, barge, pipeline, rail car, and truck.
7 |  |  | Describe in detail the manner in which material will be handled from shipside direct to the facility, from shipside via highway to the facility, from airport via highway to the facility, or from railroad to the facility.
8 |  |  | Discuss any laws or regulations governing the handling, shipping, loading, and unloading of products from the facility.
9 |  |  | Will feedstock be required to go into bonded tanks?
10 |  |  | Will customs inspectors be at the facility?
11 |  |  | Will tanks be gauged or will meter readings be accepted?
12 |  |  | Provide information on the availability and method of supply for various materials required for facility operation and maintenance, particularly chemicals. Provide information on the availability of alternate suppliers to understand the business interruption risks. For example: | Includes description of the means of feedstock and product transportation (truck, rail, ship, pipeline, by company owned means or contract).
13 |  |  | Feedstocks
14 |  |  | Acids
15 |  |  | Bases
16 |  |  | Specialty chemicals (inhibitors, HF, aluminum pyrophoric catalyst, initiators, regulated substances, etc.)
17 |  |  | Specialty gases (Nitrogen, Oxygen, natural gas, propane, etc.)
18 |  |  | Lubricants (greases, oils, etc.)
19 |  |  | List cargo sizes and frequencies of shipments in and out of the site.
20 |  |  | How will raw materials and supplies be delivered and received?
21 |  |  | Consider special areas for fork lift truck traffic - both indoor/outdoor.
22 |  |  | How will materials and supplies be distributed and transported within the facility?
23 |  |  | How will intermediates and products be stored and shipped?
24 |  | 4.16.3 | Pipeline Issues
25 |  |  | Review existing underground piping into, within, and leaving the facility, including
26 |  |  | Utilities (e.g., natural gas, electric cable) | Utilities: See Questions in Table D.8, Section 4.18
27 |  |  | Water (e.g., sanitary sewer, chemical treatment sewers, water mains, rainwater water runoff, river discharges, etc.)
28 |  |  | Topographical data (e.g., soil conditions, frost penetration depths)
29 |  |  | Local pipeline preferences
30 |  |  | Review existing overhead piping into, within, and leaving the facility, including
31 |  |  | Utilities
32 |  |  | Feedstock from or products to adjacent facilities
33 |  |  | If pipelines are required for feedstock or products, submit information on the following:
34 |  |  | Determine the preferred route and entry into the facility.
35 |  |  | Are there rights-of-way requirements? (must be considered in total land area required for the facility)
36 |  |  | Does the preferred route require crossing flood plains, flood levees or navigable waters where boring may be required?
37 |  |  | Should lines be buried or aboveground?
38 |  |  | What regulations apply to pipelines? What are the local minimum clearance requirements from roads and highways? If buried, what is the depth required?
39 |  |  | Are there any unusual problems, such as rock excavation, quicksand, sinkholes, or corrosion protection issues?
40 |  | 4.16.4 | Truck Transportation Issues
41 |  |  | Describe the highways and roads in the locality. Can the existing highway handle the anticipated construction loads and the increased traffic loads once the facility is operating?
42 |  |  | Will a new road have to be built to connect the facility with the local highway system?
43 |  |  | Determine the maximum allowable loading on roads and bridges.
44 |  |  | Estimate the distance to nearest express and freight yard.
45 |  |  | Are there any restrictions or curfews on the use of the roads or seasonal load limits?
46 |  |  | Can local roads accommodate the width required for trucks, including for making right turns?
47 |  |  | What are the pertinent regulations on ownership and use of passenger and truck vehicles in the area?
48 |  |  | What public transport is available to and from the facility?
49 |  |  | What private trucking services are available?
50 |  |  | Evaluate trailer weigh scale needs, including number of scales, additional building for printer and instrumentation associated with weighing truck trailers.
51 |  |  | Will peak congestion periods on public roads increase transportation risks? | Consider land for onsite parking and holding area.
52 |  |  | Will one-way traffic flows need to be developed?
53 |  |  | Evaluate the use of trailer tracking bar-code scanners and cameras with computer access by security and logistics personnel. | Note: At United States locations, these can be used for DHS listed chemicals.
54 |  |  | Evaluate the use of locking gates on border between the facility and truck entry (for example, propane terminals that are not manned 24 hours per day). Includes gates/arms to prevent crossing during emergency conditions.
55 |  | 4.16.5 | Railroad Transportation Issues
56 |  |  | Obtain copies of any regulations covering permissible proximity to tanks or existing facility equipment including operating units.
57 |  |  | Obtain copies of regulations regarding LPG, toxic gases or liquids, etc.
58 |  |  | Determine the names and types of railroads (electric, diesel, steam) serving the facility area.
59 |  |  | Determine length of spur that would have to be constructed to the facility.
60 |  |  | Submit drawings showing proximity and extent of marshalling operations.
61 |  |  | Determine the gauge of track in the area, spacing of tracks, and weight of rails. Obtain a sketch showing the design of rails and railroad ties (wood or concrete) that should be used within the facility.
62 |  |  | Determine the minimum clearance for railroads between tracks, from structures, and overhead.
63 |  |  | Determine the normal platform height and clearance between car and platform or building for loading and unloading.
64 |  |  | Obtain the normal load-carrying capacity of rail cars that may be required during construction and/or for shipping product. (both by weight and by volume)
65 |  |  | Determine the maximum axle loading permitted on rail cars.
66 |  |  | Furnish outline drawings with dimensions of cars handling special materials such as catalyst, cement, caustic, ammonia, acid, SO2, and the like (list possible items which may be hauled).
67 |  |  | Obtain a schedule of freight rates.
68 |  |  | Discuss arrangements that can be made with the railroad company for railroad tracks inside the facility. For example, will the railroad company:
69 |  |  | Supply material and install railcar tracks?
70 |  |  | Handle movements of rolling stock with their own locomotive during construction and/or during facility operation?
71 |  |  | Rent to the facility a locomotive for temporary use during construction? If so, obtain rental rates and characteristics of rental locomotive (draw bar pull and axle loads.).
72 |  |  | Will the company or railroad operate the facility siding? Who will provide marshalling yards or drill service?
73 |  |  | What is the minimum and maximum number of filled or empty cars that could constitute a direct train from the facility siding? How often could the cars be spotted (number of deliveries per day) and what is the average size train?
74 |  |  | Will the full railcar inventory need to be managed, preventing accumulation and exceedance of a hazardous material?
75 |  |  | Is there a railcar staging area?
76 |  |  | Do different railcar contents need to be segregated from each other?
77 |  |  | Is there a management system to prevent exceeding the limit?
78 |  |  | Has railcar congestion been considered in the deflagration / explosion modeling?
79 |  |  | Will the rail yard spacing be large enough so its design can minimize explosion risks from leaking rail cars and/or located far enough from the high hazard process areas to minimize the possibility of drifted clouds?
80 |  |  | Will the addition of a rail spur or sidings interfere with community grade crossings (e.g., blocking a grade crossing for any significant amount of time which can cause traffic delays)?
81 |  |  | Evaluate railcar weigh scale needs, including number of scales, additional building for printer and instrumentation associated with weighing railcars.
82 |  |  | Evaluate the use of railcar tracking bar-code scanners and cameras with computer access by security and logistics personnel. | Note: At United States locations, these can be used for DHS listed chemicals.
83 |  |  | Evaluate the use of locking gates on border between the facility and railroad hand-off. Includes traffic evaluation for both foot and mobile equipment crossing the railroad, derailers, and gates/arms to prevent crossing during emergency conditions.
84 |  | 4.16.6 | Port Operations Issues
85 |  |  | How many and what type of vessels (including ocean-going tankers of various types, coastal tankers, barges, or bunkering vessels) will be required to move feedstock and products?
86 |  |  | What is the size (length, draft, and beam) of typical available vessels that might be employed?
87 |  |  | Determine the weather operating envelope for the vessels and berth facilities so that estimates of weather related downtimes can be prepared.
88 |  |  | What specific requirements will need to be provided by the new facility to support the vessels? (for example, ballast water or bunkering systems)
89 |  |  | Furnish pertinent information (published data, if available) on:
90 |  |  | Soundings
91 |  |  | Tides
92 |  |  | Floods | Note: If local roads are subject to flooding, consider alternate routes to reduce logistics and personnel accessibility disruptions.
93 |  |  | Traffic conditions
94 |  |  | Silting conditions
95 |  |  | Type of harbor bottom
96 |  |  | Dredging
97 |  |  | Bulkheads
98 |  |  | Salt water spray/deposits
99 |  |  | Tidal information should include yearly average high and low, and extreme high and low tides on record with discussion of meteorological conditions causing the extremes. Include a copy of tide tables for the area, if available.
100 |  |  | Supply map of harbor showing harbor boundaries, pier head lines, channels, soundings, and river velocity.
101 |  |  | Is protection (such as traveling screens) required against harbor debris?
102 |  |  | Marine Accommodations
103 |  |  | Describe the port facilities. What draft, length, and beam ships or barges can be accommodated?
104 |  |  | Describe the facility jetty/docking facilities, if available. What space is available for piers or jetties/docks? Are any alterations desirable? Will a harbor basin need to be constructed?
105 |  |  | What are the waterway conditions: details regarding harbor boundaries, channels, soundings, current measurements, tides and flood conditions, tidal waves, and peak waves caused by storms.
106 |  |  | If there are any government-owned or other marine operations which will be utilized by the company, furnish a complete description, outline basis on which company will rent them, and give design stresses, allowable pull on bollards, and details of jetty/dock construction.
107 |  |  | Discuss availability of, regulations regarding, and need for tugboats.
108 |  |  | What are the pilot regulations and how will the facility accommodate the regulations?
109 |  |  | Any regulations on clearances between adjacent tanks or barges at piers or with regard to onshore buildings? For example, can barges be loaded side-by-side?
110 |  |  | Estimate average demurrage associated with awaiting tide, fog, weather conditions, or any other factors.
111 |  |  | If required, is steam, electric power, or firewater available at the piers or barge facility? If so, in what quantities?
112 |  |  | Evaluate the needs for marine vessels and marine crews
113 |  |  | Instrumentation
114 |  |  | Building for printer and instrumentation
115 |  |  | Utilities
116 |  |  | Lighting
117 |  |  | Storage areas with foundations/roofs
118 |  |  | Potable water and sewerage systems
119 |  |  | Automatic cleaning and purging systems and monitors for LEL and oxygen
120 |  |  | Temporary accommodations (e.g., a place to sleep and shower)
121 |  |  | Access paths away to/from facility for crew members
122 |  |  | Consider the use of maritime tracking bar-code scanners and cameras with computer access by security and logistics personnel | Note: At United States locations, these can be used for DHS listed chemicals.
123 |  |  | Consider the use of locking gates on facility jetties/docks.
124 |  |  | Consider traffic evaluation both foot and mobile equipment accessing jetty/dock.
125 |  |  | Consider gates/arms to prevent crossing in emergency conditions.
126 |  |  | Consider the use of 3rd party maritime companies for logistics, including loading and unloading vessels, pickups, traffic patterns, parking, etc.
127 |  |  | Consider adding video surveillance to marine jetties/docks
128 |  |  | Consider marine dock emergency response (e.g., personnel nearby for timely response to pool fires, jet fires, etc.; escape routes for jetty/dock personnel, etc.)
129 |  |  | Marine regulations
130 |  |  | Are there any special regulations applicable to the waterways?
131 |  |  | For example, in the United States, “navigable waterways” have regulatory requirements requiring additional permitting, record keeping and reporting. This may apply to areas prone to flash flooding. A rare but important (and sometimes potentially very restrictive) consideration relative to facility siting may exist. When looking into a site, or a major expansion at a large site with significant land, be aware of and search out any listed “navigable waterways” that could be impacted. Be aware that this category of navigable streams is defined as navigable in law but not actually navigated other than by log rafts, or even just logs, and the “stream bed” might normally be dry. [Reference interpretations of Title 33 Code of Federal Regulations sections 2.10 and 1321] On occasion, for some political reason, a dry wash or similar land characteristics that naturally or by design is used to carry or divert heavy rain or snow-melt run-off is designated as a “navigable waterway.” Construction activities may be limited or otherwise restricted, and set-backs can be much more than normally expected.
132 |  |  | Cargo Handling
133 |  |  | Are barges available for construction purposes?
134 |  |  | What is the maximum size and weight vessel that can be handled by:
135 |  |  | Barge?
136 |  |  | Railroad?
137 |  |  | Truck (via highway)?
138 |  |  | Diameter
139 |  |  | Length
140 |  |  | Weight
141 |  |  | What systems are available for unloading and storing construction materials and equipment? How will ships’ stores be handled, if required? Fresh water? Crew amenities?
142 |  |  | Submit information on cargo-handling facilities available, such as floating cranes, lighters, stevedoring charges.
143 |  |  | Are there any regulations as to hours when tankers or barges can enter or leave, or during which they can unload or load? What are the demurrage charges?
144 |  |  | Is railroad siding available near the jetty/dock?
145 |  |  | How will governmental customs requirements and access in port or at the site be addressed?
146 |  |  | Marine Repair Facilities
147 |  |  | What marine repair facilities are available in the vicinity?
148 |  | 4.16.7 | Air Carrier Issues
149 |  |  | Where is the nearest cargo and passenger airport? What is the distance to the facility?
150 |  |  | What is the availability and prospect for using helicopter transport to the facility?
151 |  |  | Does a nearby airport present a hazard due to its takeoff and landing paths?
152 |  |  | Is there a height or zoning restriction on the airport approach that could impact flares, large towers or structures? Are warning lights required
153 |  |  | Could activated/open safety valves generate dispersions in the approach path for an airplane?
154 |  |  | Is the elevated flare dispersion (for an unignited release such as a flare pilot failure) in the glide path for the approach of an airplane or the takeoff path from the airport?
155 |  |  | Does the airport have a master expansion plan (future runways) that would infringe on the plot space considered?

## Appendix D - Table D.7
Appendix D - Table D.7 - Checklist for Communication and Design Issues
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.17 | Communication Issues
2 |  |  | What languages are used in communication?
3 |  |  | Location of services that may be subject to interference from a new facility or may interfere with the communication or operation of the facility. These may include radio, television, cell phone or microwave communication equipment.
4 |  | 4.17.1 | Types of communication systems
5 |  |  | Telephone systems – Provide the following information.
6 |  |  | Describe local phone system as to type (manual or automatic) and adequacy for handling increased traffic. Is cell phone service available and if so, identify the service providers and current generation (analog, 2G, 3G, 4G LTE, 4G, 5G, etc.)?
7 |  |  | Give information on rental rates and opinion as to advisability of installing a facility-owned intra-site telephone system or renting a system installed and owned by the telephone company. If rental basis is feasible, would it include private, automatic or manual, exchange switchboard and instruments? What operations would have to be provided by the facility?
8 |  |  | Internet Systems – Determine what internet communication support is available: phone lines, broadband, cable, ISDN.
9 |  |  | Microwave Communications – Are microwave systems required due to the lack of telephone and internet support?
10 |  |  | Radio communications - What laws or regulations govern its use?
11 |  |  | Are there available frequencies?
12 |  |  | What other users could provide interference?
13 |  |  | How secure are the channels?
14 |  |  | Do regulations permit use of two-way radios in the facility and in truck cabs?
15 |  | 4.17.2 | Data retrieval systems
16 |  |  | Will electronic data acquisition devices or data loggers pose area electrical, hazardous area classification issues?
17 |  | 4.17.3 | Packages and mail-related courier services
18 |  |  | For delivery of physical items (letters, critical drawings, design packages, samples, parts, etc.), is there a local mail service and/or global mail service available?
19 |  |  | If local/global mail services are available, how far is the nearest service from the facility’s location?
20 |  |  | Is overnight service available?
21 |  |  | If there is no mail service, identify how packages will be delivered. Options to consider: company plane, pilot and flights daily to and from major cities. If speedy delivery is important, investigate what is available and the quality of the service beforehand, especially for remote locations.
22 | 4.18 | Engineering Design Issues
23 |  |  | Measurement Systems
24 |  |  | What system of measure will be used for calibrating instruments? (Metric?)
25 |  |  | What weights and measures system is used in the area or facility?
26 |  |  | What system of measure will be preferred by local inspectors and local engineering companies to develop and approve construction drawings?
27 |  |  | What system of measure is likely to be preferred locally for facility instrumentation, drawing and procedure development?
28 |  |  | Codes, standards, design factors, and units
29 |  |  | Identify any local codes or regulations which must be followed with regard to:
30 |  |  | Structural steel and reinforced concrete
31 |  |  | Architectural design
32 |  |  | Pressure vessels
33 |  |  | Electrical design
34 |  |  | Piping
35 |  |  | Boilers
36 |  |  | Plumbing and sanitary systems (architectural)
37 |  |  | Working conditions such as air changes, working temperatures in building, or safety requirements
38 |  |  | Spacing of process units, tank firewall capacity, and sewer connections
39 |  |  | Permissible noise level. | Noise: See Questions Table D.4, Section 4.13.6
40 |  |  | Health ordinances
41 |  |  | Specific suppliers for raw materials
42 |  |  | Specific suppliers for natural resources
43 |  |  | Specific suppliers for fabricating equipment
44 |  |  | Are there design standards applicable in place of the corresponding local codes? | For example, Internal company standards or standards listed in Appendix A of this Guideline
45 |  |  | What are local approval requirements for building designs? Identify the prevailing type of architecture and typical materials of construction. Are codes applicable for temporary constructions?
46 |  |  | Can imported steel be used instead of steel made to local specifications? Obtain booklets on local shape, weight, and standard sizes. State whether Bessemer or open-hearth steel will be required.
47 |  |  | Are there any local piping preferences, codes or standards which will affect design according to the company standards?
48 |  |  | What is the local regulation or practice regarding wind load used in design? What wind velocity do local authorities require? What snow loads are used in design?
49 |  |  | Is a corrosion allowance used locally in structural steel design?
50 |  |  | What standard system of units and measures should be used?
51 |  |  | What languages are used in communication and design documentation?
52 |  |  | Define the automation level: will the plant be fully automated versus manual? (This will affect spacing and layout.)
53 |  |  | List the design concepts employed in developing the process that may affect the layout and spacing of the site, i.e. enclosed loading vs. outside loading.
54 |  |  | List known process technologies that will be employed.
55 |  |  | Identify the turnaround philosophy (shuts down once every two years, or continued operation with individual process shutdowns as required).
56 |  |  | Identify the expected life of the plant (10 year, 20 year, or other).
57 |  |  | Identify the desired operation mode (5-day/week; 24hr 7 days/week; utility; uptime; or on-stream factor).

## Appendix D - Table D.8
Appendix D - Table D.8 - Checklist for Utilities Concerns
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.19 | Utilities Issues
2 |  |  | For all utilities: Consider routes and tie ins to get secure supplies of reliable utilities. | Note: May require specific utility scope, including rights-of-way, land purchase/lease/compensation, and additional facility land requirements.
3 |  | 4.19.1 | Electric power supply
4 |  |  | Name and address of the utility. Name and position of contact person(s).
5 |  |  | Present and future power availability and reliability.
6 |  |  | Applicable rate schedules, including fuel adjustment clauses, demand charges, labor and power factor clauses, government taxes, and contract duration.
7 |  |  | Is an interruptible power supply contract available that could provide lower power costs?
8 |  |  | Is it permissible for the new facility to generate all or a portion of its power requirements with the public utility system providing the balance?
9 |  |  | What are the rates and charges for provision of both partial and full standby power for on-site generation? | Dust restrictions may apply to coke, coal and power stations. See Table D.4, Section 4.13.2.
10 |  |  | Are there governmental bodies or regulators requiring new facilities to participate in power exporting to the power grid network?
11 |  |  | Will the new facility or the utility will be responsible for providing the main substation, including real estate and civil work?
12 |  |  | Applicable investment charges for facility utility-installed operations.
13 |  |  | Type and voltage level of the utility service feeders, and whether the feeders will be radial or loop type. Where a radial feed system is to be installed, will the utility install two independent feeders?
14 |  |  | Maximum and minimum interrupting level (kVA or MVA) of incoming service.
15 |  |  | Type and main substation transformers to be installed, and whether transformers will have automatic load tap changers or manual no-load tap changers.
16 |  |  | Availability of construction power, the applicable rate schedules, and the necessary systems to be provided.
17 |  |  | Maximum allowable voltage-drop on motor starting or group reacceleration.
18 |  |  | Regarding public utility power, determine:
19 |  |  | Amount available | kW
20 |  |  | Characteristic | phase
21 |  |  | Characteristic | cycle
22 |  |  | Characteristic | volts
23 |  |  | What is the minimum and future maximum short circuit level kVA at the source and/or the adjacent facility (s) that will be sharing the utility power?
24 |  |  | Reliability of power supply based on past performance? (unplanned outages per year, planned outages per year, length of outages, and percent voltage variation)
25 |  |  | What is the distance from the new facility property limits to substation(s) from which the utility would supply power?
26 |  |  | How many feeders would the utility install from substation(s) to the new facility limits?
27 |  |  | What are the feeder characteristics regarding construction method? Are feeders underground or overhead?
28 |  |  | Would the new facility have exclusive use of feeders?
29 |  |  | If feeder voltages were too high for the new facility, would the cost of this substation be borne by the utility or the new facility?
30 |  |  | What voltage will the new facility require for:
31 |  |  | Lighting
32 |  |  | Small motors [below ____________ kW (hp)] | Use company guidance for "Small" and "Large"
33 |  |  | Large motors [above ____________ kW (hp)] | Use company guidance for "Small" and "Large"
34 |  |  | What are the nominal standard secondary distribution voltages available in the range of 400 volts to 11,000 volts?
35 |  |  | The types of local power distributor equipment.
36 |  |  | What are the characteristics of available power transformers as to:
37 |  |  | Voltage ratings and sizes in the 300kVA to 2,500-kVA range?
38 |  |  | Impedance of various sizes and ratings?
39 |  |  | What are characteristics of available switchgear as to:
40 |  |  | Standard voltage ratings in the 400-volt to 11,000-volt range?
41 |  |  | Continuous current, interrupting current, and momentary current ratings of various-sized circuit breakers?
42 |  |  | Will the public utility provide power during construction?
43 |  |  | As natural disasters can damage public power systems extensively (months), can the facility startup without public power (or limited public power) after a natural disaster (flood, hurricane/typhoon, earthquake)? [CCPS 2015]
44 |  | 4.19.2 | Water supply
45 |  |  | Give volume available from various sources and types such as:
46 |  |  | Salt water
47 |  |  | Brackish water
48 |  |  | Industrial raw water | Note: The quality of raw water may vary with seasons (salts and particulate levels). Consider options for raw water treatment systems.
49 |  |  | Fresh water
50 |  |  | Well water
51 |  |  | Municipal supply (Source for drinking water - potable water, sanitary water, boiler makeup, and fire water)
52 |  |  | Are there restrictions on ground water draw and extraction rates, especially in areas of agricultural and public demand? | Consider reliability of supply over plant life risk of dwindling water table with competing takers over seasons and years.
53 |  |  | Provide daily water temperatures for the hottest month and monthly temperature ranges for the balance of the year.
54 |  |  | If available, furnish analyses of water from each possible source of supply, including hardness, suspended solids, pH value, and amount of corrosive agents. Determine if the water will require chemical protection against algae.
55 |  |  | If water wells are to be drilled, determine information for:
56 |  |  | Whether there are regulations limiting the amount or use of well water.
57 |  |  | Aquifer water pressure to determine if the water wells will be free flowing, at the pressure and volume required.
58 |  |  | Depth to the aquifer.
59 |  |  | Allowable spacing between adjacent water wells.
60 |  |  | What is the cost of municipal water?
61 |  |  | What is the maximum amount of municipal water that may be purchased?
62 |  |  | Are there local regulations on drinking water supplies?
63 |  |  | Are there local water shortage and rationing plans?
64 |  |  | What are the triggering values?
65 |  |  | Who is included in the rationing?
66 |  |  | What would be the impact of these plans on the facility’s water supply needs?
67 |  |  | Are there building codes or other regulations that limit the height of structures such as water towers?
68 |  | 4.19.3 | Steam supply
69 |  |  | Is steam available from sources outside the facility? If so, at what pressures, quantities, and cost?
70 |  |  | If steam is purchased, furnish drawings showing location of the steam utility systems in relation to the planned facility.
71 |  |  | Will an outside steam source utilize fuel or burnable waste products generated by the new facility?
72 |  |  | Are there any rules, regulations, or standards that may apply for steam utility system construction? These may include piping, boilers, exhaust systems, and condensate handling.
73 |  | 4.19.4 | Fuel supply
74 |  |  | Determine the availability, reliability, supply points, heating values, costs, and analysis of fuel commonly used in the area.
75 |  |  | Determine supply sources, pressures, temperatures, and fuel specifications, if available.
76 |  |  | Determine the needed fuel supply systems (storage tanks, pipelines, and unloading systems).
77 |  | 4.19.5 | Air supply
78 |  |  | If air separation operations are needed, determine the quantities of ambient air ingested through the process unit intakes. | Note: Air separation operations located downwind of other areas emitting contaminants may result in accelerated corrosion, processing issues, and safety issues.
79 |  |  | Is the air supply used for fire water deluge/sprinkler system design? Consider special backup designs for these fire protection systems if the air supply is lost.
80 |  | 4.19.6 | Other utility supplies
81 |  |  | Are other special utilities required? (e.g., nitrogen, hydrogen, or oxygen)
82 |  |  | If so, determine if they
83 |  |  | Will be transported to and stored at the facility, or
84 |  |  | Will be generated at the facility.

## Appendix D - Table D.9
Appendix D - Table D.9 - Checklist for Other Concerns
Issued 06-April-2018
Line Item | Section in Chapter 4 |  |  | Details or n/a | Action? (Yes/No)
1 | 4.2 | Other Issues
2 |  | 4.20.1 | Personnel
3 |  |  | What are the local customs, traditions and holidays?
4 |  |  | Will accessibility to a remote location pose issues due to travelling distance for personnel?
5 |  |  | Engineering companies
6 |  |  | List local companies available to handle facility construction engineering work for:
7 |  |  | Soil investigation
8 |  |  | Process Unit construction
9 |  |  | Utilities construction
10 |  |  | To what extent are these companies familiar with internationally accepted practices and standards (for instance, ANSI standards)?
11 |  |  | What similar jobs have they performed in the past?
12 |  |  | For whom have they performed these jobs?
13 |  |  | What engineering firm qualifications are required (i.e., per corporate guidance)?
14 |  | 4.20.2 | Other support personnel and operations
15 |  |  | Contractors
16 |  |  | List companies that will be available locally to handle:
17 |  |  | Location preparation (hydraulic fill or earthmoving)
18 |  |  | Erection of tankage
19 |  |  | Jetty/dock and terminal facilities
20 |  |  | General field labor contracts for process and off-site work
21 |  |  | Housing, shops, warehouse, offices, lab and other buildings
22 |  |  | To what extent can the new or existing facility organization handle construction supervision?
23 |  |  | Are there any laws or regulations govern the use of foreign or expatriate contractors?
24 |  |  | Are any of these contractors or engineering companies affiliated with international engineering and construction companies?
25 |  |  | Construction and Maintenance Labor
26 |  |  | Are there local labor laws or regulations (i.e., work day length limits)?
27 |  |  | Are similar projects available for review to estimate the cost of construction at the facility? | Examples may be available from local contractors or adjacent facilities. These may include the cost of civil work, facility preparation, tank erection, and buildings of different construction.
28 |  |  | Are similar projects available for review to estimate the cost of operations and maintenance at the facility?
29 |  |  | For each of the following crafts, what is the availability of skilled crafts workers and is there a history of labor issues impacting cost and schedule?
30 |  |  | Common labor
31 |  |  | Carpenters
32 |  |  | Bricklayers
33 |  |  | Welders (acetylene)
34 |  |  | Welders (electric)
35 |  |  | Pipe fitters
36 |  |  | Boilermakers
37 |  |  | Structural ironworkers (riveters)
38 |  |  | Cement workers
39 |  |  | Electricians
40 |  |  | Instrument specialists
41 |  |  | Insulators
42 |  |  | Crane operators
43 |  |  | Riggers
44 |  |  | Heavy equipment operators
45 |  |  | Truck drivers
46 |  |  | Mechanics
47 |  |  | Machinists
48 |  |  | Painters
49 |  |  | Plumbers
50 |  |  | Will a premium need to be paid to attract workers to the area?
51 |  |  | Discuss availability and source of supervisors and foremen. What amount of outside (of the area) supervision will be required?
52 |  |  | What is the estimated optimum ratio of outside (of the area) to native labor for facility construction work?
53 |  |  | Will it be necessary or desirable to establish training programs in the crafts required for construction work?
54 |  |  | Are there any racial problems or discrimination that need to be taken into account?
55 |  |  | What percentages of local workers speak or understand different languages (e.g., English)?
56 |  |  | Is night work permitted?
57 |  |  | Address issues with contractor training costs.
58 |  |  | Note: In the United States, there may be additional costs if the area has not yet had any coast guard involvement, the TWIC card is required, and a qualified training center is not located nearby. There have been cases where the company has had to pay for this training to qualify its construction and future construction/maintenance contractors so that they can work on the property.
59 |  |  | Operations Personnel
60 |  |  | What languages are used?
61 |  |  | To what extent can personnel speak and write the language used for facility labeling and documentation? | (Consider that labeling and documentation may need to be translated into local language/dialect.)
62 |  |  | Have the operations-related “essential” personnel been identified? | (References include API RP 752, API RP 753, API RP 756, and CCPS 2012b)
63 |  |  | Discuss the availability of personnel required for the permanent facility staff in categories such as the following:
64 |  |  | Process operators
65 |  |  | Maintenance crafts workers (see craft listing above, includes mechanics and electricians)
66 |  |  | Engineers (chemical / process, environmental, mechanical, civil, reliability)
67 |  |  | Technical specialists (occupational safety, industrial hygienists, quality)
68 |  |  | Laboratory technicians
69 |  |  | Emergency responders, both for the facility or from external organizations (fire fighters, emergency medical technicians - EMTs, and hazardous material release responders - "HAZMAT" teams)
70 |  |  | Doctors and nurses, both for the facility or from external organizations
71 |  |  | Security
72 |  |  | Support staff (administrative, accountants, clerks, draftsmen, etc.)
73 |  |  | Location Support Operations
74 |  |  | List the prices of heavy construction equipment and tools that can be made available by the facility organization, local contractors, or manufacturers. Are guy derricks available locally?
75 |  |  | What is the rental cost for such equipment? Is the operator included? Are qualified operators available for the equipment?
76 |  |  | Are garage services and spare parts available locally for international equipment?
77 |  |  | Are there any restrictions against the use of heavy mechanical equipment?
78 |  |  | Shops/Maintenance Operations
79 |  |  | To what extent can facility maintenance work be handled by outside contractors?
80 |  |  | What type and class of work can be done by outside shops?
81 |  |  | Where is the location of outside shops relative to the facility?
82 |  |  | What is the local manpower availability for turnaround work?
83 |  |  | Are there special seasonal needs requiring facility or contractor resourcing?
84 |  |  | Lawn maintenance
85 |  |  | Weed control
86 |  |  | Rodent, pest, insect control
87 |  |  | Snow removal
88 |  |  | Sandstorm sand removal
89 |  |  | Construction Materials and Equipment
90 |  |  | Are there seasonal peak times for construction activities and rentals (i.e., during summer months in areas with very cold winters)?
91 |  |  | Indicate the quantities and types of construction materials that are locally available, for example, which local companies can be used for mixing concrete?
92 |  |  | Are any of these materials available as surplus in nearby affiliate companies?
93 |  |  | What restrictions are there on importing any of these materials and other equipment such as pumps, exchangers, drums, towers, and motors? Are any of the latter made locally? If locally made, ensure that there is a Quality Assurance/Quality Control (QA/QC) plan in place on locally made equipment, especially if the equipment design requires meeting ANSI or other standards. If there is no QA/QC for local suppliers, the operations may have costly equipment integrity issues once in operation.
94 |  |  | Is warehouse space for materials available or must this be erected?
95 |  |  | What material and equipment required for construction can be purchased locally? Are foundries, boiler shops, machine shops, and steel fabricating companies available locally, and in what capacity? If so, see local QA/QC issue discussion in line item 7.3.6.3 above.
96 |  |  | What governmental restrictions, regulations, priorities, or allocation supply may impact availability of supply allocations?
97 |  |  | Local resources
98 |  |  | In what language is the local workforce fluent?
99 |  |  | Are qualified operations and maintenance staff and workforce available in the region?
100 |  |  | Are qualified construction personnel and support contractors available in the region to support the development and operation of the Process facility?
101 |  |  | Consider what level(s) of training and competency capability may be needed, especially in remote locations.
102 |  |  | Does the local community have sufficient resources (housing, medical, etc.) to support the needs of the construction and operations personnel that will be needed for the project?
103 |  |  | What encroachment and moving-on policy should be developed for squatters, temporary camps and entrepreneurs who set up shop during construction (and may extend into operations)?
104 |  |  | What languages are used in communication and design documentation?
105 |  |  | Will the site be shared with another operation? If so, with whom?
106 |  |  | List other shared or owned operations, staff, and/or facilities on the new site | For example: office buildings, day care facilities, warehousing, storage facilities, utilities, security staff, maintenance staff, site management staff, and emergency response staff and equipment.
107 |  |  | Will shared operations have common entrances/exits or separate rights-of-way.
108 |  |  | If facility location is on leased land, are there owner restrictions for construction and operation? | For example: For construction/operational hours and owner policies (e.g., access to facility, permits to work, owner-enforced safety rules, etc.).
109 |  |  | Identify the turnaround philosophy (shuts down once every two years, or continued operation with individual process shutdowns as required).
110 |  |  | Accessibility noted here for future growth (sufficient staffing in area?)
111 |  | 4.20.3 | Housing
112 |  |  | For remote facilities, is housing available for both construction personnel and for facility employees and their families once in operation?
113 |  |  | To what extent will permanent housing be required for employees?
114 |  |  | Where will the permanent housing be located?
115 |  |  | Are available schools, day care centers, nursing homes, hospitals, shops, and recreational areas nearby?