## PSSR Checklist
PSSR Category / Item | Applicable? (YES / NO and Why) | Action Item Description(s) | Assigned to: | Due Date
INSTRUCTIONS (Issued 6-March-2025) Click the number 1 at the far left of the screen to hide all items and see only the categories. Click the number 2 at the far left of the screen to reveal all items under all categories. If a category does NOT apply to your review, click the minus sign next to it to hide questions.
1) System Checkout Items
Complete/document quality assurance program:
Received equipment specs as purchased
Adherence to design drawings/specifications
Materials of construction
Workmanship
Equipment components checkout/commissioning (document)
Loop and interlock/permissive/alarm: set point adjustment and testing (document results)
Instrument calibrations done and documented
Validation protocol developed, approved and executed
Pressure testing done and documented
System cleaned and flushed
Fire protections systems inspected, acceptance tested documentation provided
Ventilation systems balanced
Performance checkout of local exhaust systems
Vibration measurements/documentation
Field radiography done and documented as required
Baseline data, such as thickness readings for pressure vessels/piping
Other baseline data
NDT reports
Water batching (document)
Review punch list for applicable actions.
2) Engineering Design Documentation
Narrative of control philosophy/Sequence of operations documentation
Instrument index
Instrument loop diagrams
Interlock descriptions
As-built drawings: P&IDs, electrical, piping, mechanical
Tabulation of process alarms, interlocks/permissive descriptions and trips with settings (P&IDs)
Review and approval of fire protections systems design
Piping specifications (P&IDs / mechanical drawings)
Pressure relief device sizing calculations
ASME code pressure vessels U-1 data sheets (to Maintenance)
Reference codes/standards for facility design
Reference codes/standards for facility installation
Design codes for specific equipment
Welder certification
NDT certification
Electrical classification drawings
Electrician certification for classified areas
3) Maintenance Items
Spare parts lists developed
Stock required spare parts
Equipment manuals/specifications to Maintenance and Operating Department
Vendor prints
Submit preventive maintenance requests (PM’s)
Service contracts in place
Train maintenance personnel and document
4) Operational Items
Develop SOP and special procedures – incorporate safety and operational issues:
Complete change control authorizations
Develop/issue operating procedures:
Initial start-up
Normal start-up
Normal operation
Normal shutdown
Emergency operations including emergency shutdown
Start-up following emergency shutdown
Start-up following turnaround
Non-routine procedures (equipment clean-out, equipment preparation for maintenance)
Auxiliary equipment operation
Train operating personnel and document
Provide technical coverage
What is the probability of containment failure? What are the subsequent consequences? Review spill containment, rainwater runoff and fire water containment.
5) Electrical Systems
Have instrumentation and electrical equipment enclosures been specified to meet the electrical classification of the area?
Have wire gauges, starters and overloads been properly sized in accordance with the National Electric Code (NEC)?
Has the design considered the requirements of electrical hot work and cranes near power lines such that outage requirements and variances will be minimized?
Has the design included adequate room for ventilation of transformers, motors, and other similar equipment?
Transformer location properly designed?
Motor control center(s) well designed?
Panel access, clearance around panel, keys etc.
Cable entry section – glanding, housekeeping and other issues
Panel power source identified? Multiple feeds?
Space heaters required?
Lighting in panels
Canopies etc. for outdoor panels
Protection settings available?
Panel board schedules
Spare capacity available?
PPE available? HV mats, gloves
Emergency/Standby power required?
VSD settings available – factory/commissioning
Room access, permitting, maintainability, ingress/egress of equipment
Pockets for drawings in panels?
Voltage warning labels?
Ventilation sufficient?
Suitability for area - IP rating, GMP suitability, hazardous area classification.
6) Pressure and Vacuum Relief
Have new or modified safety relief device(s) or vent system(s) been designed in accordance with Plant Engineering and Site requirements?
Has potential for external pressure (vacuum) from sudden cooling, condensing, pump-out, during clean-up or preparation of equipment for maintenance, or potentially submerged overflow line been addressed?
Have only full-port valves been specified for use at the inlet and outlet of pressure/vacuum relief devices?
Have any changes to safety relief device inlet or outlet piping been properly reviewed?
Will adequate facilities (alarms, detectors, redundancy, and others.) be provided to minimize the risk of a relief device actuating due to equipment, instrumentation, or utility failure?
Have the discharges of safety relief devices been located so as to avoid potential personnel injury and damage to associated equipment?
Has the design included installation of the safety relief valve vertically?
Are there standard markings on the P&IDs?
Do relief lines vent to a safe location?
Are relief lines and relief devices secured and adequately sized?
Are there any isolation valves, which will inhibit operation of relief valves if closed? If YES nominate Operations to monitor. If NO record no.
Is there a standard operating procedure for relief devices in place?
7) Field Verification
Is lighting sufficient?
Is emergency lighting sufficient?
Are steam pipes, valves or traps situated within proximity of people insulated?
Is all instrumentation identified and tagged?
Is there any rusted or damaged equipment?
Are swing gates installed on top of ladders or on access platforms?
Review edge protection on platforms and heights. Will it protect personnel and equipment? Is access adequate?
Do safety showers provide a hazard to people (slips), product (contamination of systems) or of ingress to electrical switchgear or equipment?
Are safety showers supplied from tempered water?
Is chemical dosing within a safe proximity of people and product?
Label all pipe lines
Label all electric switches, disconnects, MCCs, Control panels, cables etc.
Label vessels (material, hazard warnings)
Seal wall penetrations
Pour conduit seals
Install fire extinguishers
Evacuation routes posted
Install appropriate area signs
Is all scaffolding and equipment removed, if general housekeeping acceptable?
If there is potential for entrapment or exposure, has an E-Stop been provided?
If full guarding is in place, has a lockable isolation device been provided?
Pest control required in room/building?
MSDS sheets required?
Sprinklers in rooms?
Single point of failure condition? Has it been identified? – Record.
8) General Safety
Have ALL appropriate personnel (Operations, Maintenance, Technical, and Supervision) received adequate and appropriate training on the equipment and operating procedures?
Has adequate and appropriate PPE (Personal Protective Equipment) been specified in the Work Procedures and/or Standard Operating Procedures.
Has the PPE been provided?
Have the PPE users been trained in the use of the PPE?
Is the training documented?
Have measures been taken to adequately guard all dangerous parts of this equipment?
Has sufficient provision been made for the electrical and/or mechanical isolation of the equipment?
Are points of isolation clearly marked/labeled and readily accessible?
Have bump/trip hazards been properly identified and adequately marked?
Have all sharp edges been removed?
Has proper guarding, handrails/barriers, been provided to prevent falls?
Have all hot/cold surfaces been adequately guarded to prevent burns?
Are all cold surfaces adequately insulated to prevent condensation drips (slip hazards)?
Are Safety Showers and Eye Wash facilities provided and adequately marked?
Are the Safety Showers and Eye Wash facilities routinely inspected?
Do the Safety Showers and Eye Wash facilities locations comply with Corporate guidelines?
Are the Safety Showers and Eye Wash facilities readily visible and accessible?
Has sufficient lighting been provided so that operation, servicing, maintenance and repair of the facilities can be carried out safely?
Are notices, dials, screens, etc. for providing operational instructions, safety warnings and emergency information provided, if required, and positioned so that they are clearly visible and easily read?
Have all overhead fixtures, for example, pipe-hangers, pipe sleeves, pipe sleeve covers, valve handles, floor opening covers, etc., which could fall or be dislodged, been properly secured?
Are all of the applicable Work Permit Procedures (Confined Space Entry, Lock Out/Tag Out, Hot Work, High Work, etc.) in place?
Have the Operating, Maintenance and Supervisory personnel been properly trained on the Work Permit Procedures?
Has the fire protection systems been inspected by the insurance company?
Has acceptance testing been completed and documented?
Is there an agreed on test and inspection program for the fire protection systems (including alarm systems)?
9) Machinery / Equipment Safety
Has the machinery/equipment been installed so that it will be stable and secure during operation?
Has all access to dangerous moving parts, or danger zones created by the equipment, been prevented by the provision of the correct guards, interlocks and/or barriers?
Have the correct safety measures been taken to prevent any risk from hot/cold surfaces, ejection of material, failure of parts and their ejection, overheating/fire?
Has safe access been provided to the equipment that requires operator and calibration and maintenance personnel access for normal operations, adjustments, service, calibration, maintenance or repair?
Have slip, trip, trap, crush, entanglement, fall, bump and cut hazards been minimized?
Is the equipment provided with the properly identified START/STOP and EMERGENCY controls that are positioned for safe operation without hesitation, or loss of time, and without ambiguity?
Is the equipment provided with a clearly identified means to securely isolate it from ALL energy sources?
10) Ergonomics
Have the workstations, workplace, or equipment been constructed so that need for stooping, bending stretching, over-reaching and working over-head during operation has been eliminated or minimized?
Has the need to lift, carry, push or pull heavy loads, or parts, been eliminated to the extent possible?
Are all display screens, dials and START/STOP/ EMERGENCY buttons positioned so that they are readily visible and accessible by the operating personnel?
Have Visual Display Screens been positioned so that interference from glare is reduced to the minimum?
Have workstations been designed and equipped so that the operator can adopt a comfortable position? (That is, able to stand, or change position and sit upright, angle at elbows and knees 90°, feet on floor.)
Labeling of equipment, piping, critical valves, field instruments, switches clear?
Location of field instruments well-designed?
Sampling points accessible?
Operator task safety analyzed?
Operator task ergonomics analyzed?
Opportunities for operator error analyzed?
Non-routine tasks evaluated?
Chemical exposure hazards addressed?
Other potential exposures addressed?
Engineering controls adequate?
Building ventilation/fresh air intakes adequate?
Toxic gas monitors, alarms operational?
Protective equipment location adequate?
Placarding readily visible?
Are up-to-date Material Safety Data Sheets available?
Have the hazardous effects of inadvertent mixing of different materials been considered (that is, has a chemical interaction matrix been prepared/updated)?
Has the process design basis been documented or updated?
Has the control philosophy and sequence of operations been documented?
Has the equipment design basis (for example, BPFs/P&IDs) been documented/updated?
Have the recommendations from safety reviews, Process Hazards Analysis (PHA), Hazards and Operability Reviews (HAZOP), CHAZOP, or others, been implemented?
Record any incomplete items.
Are all relief devices shown on the P&IDs?
Are standard markings used on the relief devices?
Are the relief/rupture pressures included on the P&IDs?
Have the pressure relief device calculations been provided?
Was DIERS technology utilized to size the pressure relief devices for all pressure vessels?
Does the sizing of pressure relief devices agreed with the calculated sizes?
Do the calculations take into the downstream piping?
Do the relief devices vent to safe locations?
Is containment provided for liquids and solids released from pressure relief devices?
Are there isolation valves that, if closed, will inhibit the operation of pressure relief devices?
If yes, Operations must establish control plans to insure that the isolation valves cannot inhibit the operation of the pressure relief devices.
Are all pressure relief devices included in the Preventive Maintenance Program?
Are the inspection and testing of relief devices in accordance with local regulations?
11) Management of Change
Has a management of change – technology/subtle change document (for example, Change of Design - COD) been approved?
Has a test authorization been approved?
Are all action items, arising from the COD, that were deemed necessary for start-up, complete?
Have all changes made during construction been recorded and authorized?
Have hazards evaluations (PHAs, HAZOP or CHAZOP) been done on all the changes made during construction?
12) Process Hazard Analysis
Have project PHAs been approved and a final project safety report been prepared?
Are all action items, deemed necessary by the PHA team for start-up, complete?
Has the project been approved as “Safe to proceed with” by the PHA team?
13) Quality Assurance
Have checks and inspections been made to ensure that critical equipment is installed properly and is consistent with design specifications and vendor’s recommendations (for example, alarm and interlock tests; equipment alignment and service to process inter-connections)?
Have quality assurance inspection reports, covering fabrication, assembly and installation, been completed in accordance with the project’s quality assurance plan and reports filed with the equipment and design basis documentation?
List specific items field checked as part of this Pre-Start-up Safety Review to ensure that:
The construction meets the design specifications.
The construction matches the drawings.
Have the following documented been provided and approved:
Instrument indexes and instrument loop diagrams?
A tabulation, including settings, of interlocks and trips (hardwire and software), process alarms and permissive descriptions?
As-built drawings covering P&IDs, electrical, piping and mechanical?
Data sheets for pressure equipment built to ASME or equivalent codes?
Welder certification?
Non-destructive test (NDT) certifications?
Electrical certification for classified areas?
14) Mechanical Integrity
Have maintenance procedures been approved?
Have maintenance personnel been trained?
Have spare parts listed been developed and entered into the SAP program?
Are there adequate inventories of spare parts, operating supplies and maintenance materials?
Have quality control procedures been approved for maintenance materials and spare parts?
Have inspections and tests, including regulatory requirements) for the following equipment been included in a maintenance schedule (for example, added to the SAP system)?
Pressure vessels and storage tanks?
Pressure relief systems, vent systems and devices?
Critical controls, interlocks, alarms and instruments?
Emergency devices (including shutdown systems and isolation systems)?
Fire protection equipment?
Piping systems (incl. Components, for example, valves, excess flow valves, expansion bellows) in critical service?
Key process-to-service tie-ins?
Electrical earthening, grounding, bonding?
MCC starters?
Emergency alarm and communication system?
Monitoring devices and sensors?
Pumps?
Lifting equipment?
Has a reliability engineering analysis been considered/ completed for critical process safety equipment?
Is the equipment inspected by any outside body and certificates on file (for example, CE marking, lifting equipment test certificates, pressure systems regulations, and other items)?
Have all commissioning tests or inspections been identified (for example, pressure or leak tests, passivating procedures)?
15) Operating Procedure and Safe Work Practices
Have standard operating procedures been prepared/updated and approved?
Do the operating procedures cover:
Initial start-up?
Normal start-up?
Normal operations?
Normal shutdowns?
Emergency operations including emergency shutdowns?
Start-up after emergency shutdowns?
Start-up following turnarounds/prolonged shutdowns?
Non-routine procedure such as equipment clean-outs and preparation of equipment for maintenance?
Auxiliary equipment operations including as examples; LEV and Ventilation Systems, Heat/Cool Skids, Water (Soft, RO, WFI, Tower, etc.) Systems, Instrument and Process Air Systems, Waste Treatment Systems, Cooling (Glycol Refrigeration) Systems, Steam Generation, and others?
Safety and operational issues?
Change control procedures?
16) Training and Performance
Has specific process (or job task) training been given to personnel?
Have training records been updated?
17) Contractor Safety
Have all contract personnel been adequately trained in appropriate: chemical awareness, maintenance and operating activities and evacuation procedures?
18) Interlocks and Alarms
Has the alarm/interlock been classified and designed by the Project Team? Did the Project Team include members of the PHA team?
Did the loop testing confirm that the alarm/interlock action proved, under all conceivable failure conditions, to be fail-safe?
Prior to this PSSR, has an interlock/critical alarm Standard Operating Procedure for testing, through to the final element, been prepared and reviewed/authorized by a competent person for each new or upgraded control system?
For alarms/interlocks with more than one software or hardware circuit, have all possible interlock routes been tested?
Has all appropriate process technology been updated (for example, interlock lists, P&IDs, logic drawings, etc.)?
Does your Control System documentation adequately specify:
All major components and their model and serial numbers?
All communication cables layout and configuration?
Any configurable or custom settings and set-up?
Has consideration been given to suitable fire detection and prevention systems for the equipment?
Do you have an appropriate procedure to ensure that your software is protected (for example, routinely archived, key/password protected, etc.)?
Has the software been properly documented and filed (for example, logic drawings, schematics, sequence/batch descriptions)?
Has all software been properly validated and tested?
Is there verification that the equipment does not re-start, either on the re-setting of a protective device such as an interlock, or the re-establishment of power after an outage?
19) Environmental
Are all secondary containment/bonding facilities adequate?
Are all material storage facilities adequate and appropriately labeled?
Have adequate arrangements been made, prior to start-up, for the identification, classification and safe disposal of all waste materials?
Have all materials, used in the system, been entered on the Area Chemicals Inventory List (or equivalent)?
Are updated Area Spill Procedures available?
Are material Unloading Facilities adequate and constructed in accordance with Corporate Safety, Health and Environmental Standards?
Is there adequate containment (110% of truck volume) in the unloading areas for bulk liquid chemicals?
Have the Corporate Environmental Guidelines been followed during the design stage of this project?
Have all waste streams been identified, quantified, analyzed and minimized?
Are all of the applicable Construction, Environmental and Operating Permits up to-date and approved?
Emissions permits
Other operating permits
20) Community Awareness and Emergency Response (CAER)
Have all necessary precautions been taken to ensure that the equipment is not a source of ignition to any flammable materials, irrespective of their source?
Are fire protection facilities adequate for example, fire extinguishers, fire walls, sprinkler systems, Alarm Boxes, etc.)?
Are Emergency Escape Routes, including ladders, adequate and properly signposted?
Is Emergency Lighting adequate?
Is sufficient Respiratory Protective Equipment, such as Escape Sets or Self-Contained Breathing Apparatus (SCBA) available?
Have Emergency Procedures been prepared and relevant personnel trained?
Is the Community Panel advised of proposed new major projects?
Has an Electrical Safety Checklist (Acceptance of Electrical Installations) been completed by a competent personnel?
Has the equipment been properly installed and constructed to Corporate guidelines and local legislation, and does it meet any special installation requirements noted on the manufacturer’s certificate?
Has equipment been designed and purchased for the conditions under which it will operate (for example, hazardous areas)?
Are all live parts adequately enclosed to prevent access?
Does grounding and bonding comply with corporate and local standards/legislation?
Have fuses or circuit breakers been provided which will automatically disconnect the supply?
Are First Aid Stations, single line drawings and PPE requirements available in Motor Control Centers (MCC), Electrical Control Rooms (ECR)/Sub-stations, as appropriate?
Have all relevant documentation and drawings (for example, P&IDs, SLDs, Schematics, equipment arrangement, I/O, logic, electrical classification and Panel Schedule drawings) been updated to reflect the current installation?
Have all new Sub-station Breakers, MCC isolators, starters or other appropriate equipment been registered on to the Site Inspection Schedule?
Communications training for key employees
Education of employees on EAP, safety, health, and environmental
Education of community on new process or change
Outreach to educate responders, government officials, EAP
Assessment of potential risks to employees from accidents
Communication of emergency planning information to LEPC
Facility tours for emergency responders
Process Safety
Current, complete documentation of process design and operating parameters
Current, complete documentation of hazards of materials and process
Use of site management of change procedure
Use of site incident investigation procedure
Documented sound engineering practices consistent with recognized codes and standards
Mechanical integrity program implemented for new unit or process change
Employee Health and Safety
Medical surveillance program tailored to meet needs of new process or change
Personnel change to Central Safety Committee needed
Pollution Prevention
A quantitative inventory of wastes generated and releases to air, water and land
Education of employees and public about the inventory and impact evaluation
Documentation that waste generation is not increased by, or is minimized in, the change or new process
Documentation that waste and release prevention objectives were included the design of the new modified process & products
Distribution
Review and training of distribution hazards with distributors
Review of transportation routing to minimized potential risks
Review with corporate transportation department
Has noise-monitoring evaluations been completed?
Has signs been posted where noise levels excess 85dB?
Are ear-plugs available near areas exceeding 85 dB?
21) Location and layout
Site Conditions
Drainage
Flood control/protection
Prevailing wind
Air or water pollution exposures
Other site conditions requiring attention
Soil protection in storage, materials handling & process areas
22) Nearby operations
Hazards from
Hazards to
23) Traffic
Vehicular/railroad/pedestrian
Clearances, hazards
Adequacy of traffic signs
24) Security
Special requirements imposed by new facility
25) Storage and Handling of Chemicals
Buried pipes, tanks or chemical sewer adequate?
Leak detection and containment adequate?
26) Above Ground Storage Tanks
Adequate secondary containment provided
Operating and maintenance access adequate and safe
Adequate and accessible manways
Unobstructed pressure/vacuum relief vents
Manifolding of vents reviewed
Documented vent sizing basis (process safety manuals)
Winterization (including instrument connections)
Adequate lighting
Labeling, placarding of hazards
Other installation details
Flammable and combustible liquids
Tank placement and spacing adequate
Steel supports requiring fireproofing
Flammable liquid breather vents provided with flame arrestors or conservation vents
No flame arrestors on emergency relief vents
Safe vent discharge locations
Vapor-space ignitions hazards
Corporate recommended/approved fire protection systems in place
Flammable gases or liquefied flammable gasses
Corporate recommended/approved fire protection systems in place
27) Bulk Dry Chemicals
Dust explosion potential addressed?
28) Tank Trucks and Railcar Unloading and Loading Stations
Spill containment and safe impounding adequate?
Access platform safety adequate?
Lighting adequate?
Grounding cables adequate?
Fixed unloading pump and backflow preventer in place?
Emergency stop button location adequate?
Connections lockable and closed
Placarding of hazards
Remotely operated emergency stop valve for vehicles carrying hazardous materials
Fusible-link fire valve on vehicles with bottom unloading of flammable
Portable fire extinguisher at ground level or flammable
Safety shower and eyewash units
Recommended fire protection systems in place
Electrical systems checked?
29) Process
Safe operator access
Building exits marked
Lighting adequate
Safety shower and eyewash units
Accessible
Located on each deck
Located in control room
Portable fire extinguishers
Accessible
Located on each deck
Located in control room
30) Process Piping
Construction appropriate for duty
Materials quality assurance (including flange bolts), if critical, during construction
Workmanship (for example, no short flange bolts)
Routing satisfactory
Adequately supported and guided
Allowance for thermal expansion/no references
No small diameter connections vulnerable to breakage/failure
Expansion bellows properly installed/piping not able to move sideways/bellowed
Undamaged during installation
Flexible piping connectors correctly installed/undamaged (for example, kinked) during installation
Necessary drains provided
Hazardous outlets plugged closed
Thermal (hydrostatic) pressure relief (including heat-traced sections)
Sight glasses and gauge glasses
External corrosion protection
Freeze protection
Insulation adequate for personal protection
Protective flange covers
Approved hoses and hose and connectors (no improvisations)
31) Process Vents
Flammable liquid breather vents provided with flame arrestors or conservation vents
Telltale pressure gauge or other indicator provided between rupture disc and relief valve where a disc is installed below a relief valve
Discharge piping from emergency pressure relief devices unrestricted by 90 degree ells,
Excessive length or flame arrestors
Provisions such as drain holes to prevent accumulation of rainwater in discharge piping
Discharge piping adequately supported to withstand reactive forces of pressure venting
Safe vent discharge locations
Manifolding of vents reviewed
Vent sizing basis; documentation
32) Ductwork
Cleanouts adequate?
33) Heat Exchangers, Jackets
Vent, drains
Thermal (hydrostatic) pressure relief
Maintenance access (tube bundle)
34) Machinery
Guarding in place?
Local emergency stop button installed?
Emergency lubrication of critical machinery adequate?
Maintenance provisions considered?
Local exhaust ventilation required for shaft seals?
35) Pumps
Backflow prevention in place?
Connecting piping adequately supported to limit forces on casings?
Seal spray protection in place?
Isolation for maintenance provided for?
Preparation for maintenance (drain and vent provided)?
36) Containment
Spill containment?
Fire water runoff?
39) Process Controls and Control Room
Control room inherent safety (vs. process hazards)
Ventilation
Emergency lighting
Fire protection
Field wiring security
System cable security
Power supply
Operator interface(s)
Alarm systems
Emergency shutdown
Communications - normal and emergency
Software access/security
Software back-up
40) Utilities Water Supply
No municipal or potable water connections to the process?
41) Steam Boilers and Distribution
Feedwater treatment chemicals handling
Gas piping routing
Combustion controls
High and low drum water level alarms provided
Bypass around Feedwater regulator accessible from operating level and located where
Drum level gauge glass can be seen
Two independent low water level trips provided for unattended boilers
Dual safety relief valves in service
Relief discharge piping adequately supported and drained
Non-return valve on steam outlet
Distribution piping - see Process piping
Condensate drainage adequate
42) Compressed Air Systems
Non-lubricated construction or non-flammable synthetic lubricants used for compressor
Discharge pressures above 100 psig
43) Electrical Systems
Have instrumentation and electrical equipment enclosures been specified to meet the electrical classification of the area?
Have wire gauges, starters and overloads been properly sized in accordance with the National Electric Code (NEC)?
Has the design considered the requirements of electrical hot work and cranes near power lines such that outage requirements and variances will be minimized?
Has the design included adequate room for ventilation of transformers, motors, and other similar equipment?
Transformer location properly designed?
Motor control center(s) well designed?
44) Standby Emergency Utility Systems
Review provisions to satisfy proceeds safety requirements
45) Waste Handling/Treatment
Inspect new facilities in the same manner as process facilities
46) Warehouse
Flammable and combustible liquids
Forklifts and Motorized Hand Trucks
Traffic safety
Non combustible fuel
Recommended Fire-Protection Systems in Place
47) Maintenance Area and Shop
General walkthrough satisfactory?
Local exhaust ventilation provided for welding
48) Locker Room and Lunch Room
Adequate space
Provisions to protect contamination of food by chemicals
49) General Process Safety
Employee Participation Statement addressed?
Process Safety Information updated?
Review of highly hazardous chemicals (HHC) and MSDSs complete?
Block flow diagram prepared?
Maximum inventories calculated?
Operating limits documented?
Equipment Information in place?
P&IDs developed or revised?
Process Hazard Analysis (PHA) report(s) complete?
All PHA action items completed?
Training plan in place?
Contractor work rules revised?
Pre-Startup Safety Review plan underway?
Mechanical Integrity plan updated?
List of critical equipment complete?
Testing program with schedule prepared?
Hot Work Permit System in place?
Site Management of Change Procedure evaluated?
Incident Investigation Plan addresses the trigger event?
Emergency Action Plan (EAP) requires revision?
Facility EAP written?
Are new chemical or process hazards or risks such that changes to existing EAP are required?
Do new facilities create any new transportation emergency response needs and are such needs in place? (Chemtrec update)
Audit Schedule in place?
50) Operating Instructions
Operating instructions clear and easily understood
Instructions adequate (complete)
Material hazards adequately covered for raw materials, catalysts, intermediates,
51) Products and By-products
Health hazards and permissible exposure levels (PELs)
Physical hazards
Handling precautions and safe handling procedures including Personal
Protective Equipment (PPE) requirements
Corrective respiratory protection specified
52) Process Hazards Adequately Described
Thermal hazards
Any other hazards
Tabulation of process alarms, interlocks and trips included
Alarm and trip settings given
Specific instruction included, or reference made to separate instructions, for
Unloading and loading of bulk materials
Auxiliary equipment operation
Operating limits clearly defined in step-by-step procedures
Control ranges/limits specified
Consequences of deviations given
Responses to deviations/abnormal conditions specified
Safe hold points specified
PPE caution statements incorporated in step-by step procedures
Use of checklists as appropriate
Up-to-date
All pages show revision number and date
Reviewed for correctness
Approved / signed by Department Manager
53) Industrial Hygiene and Personnel Health
Does the design adequately consider medical, industrial hygiene, ergonomic and GMP
factors (heat stress, biological stress, high noise level, poor lighting, adequate ventilation, potential of oxygen deficient atmosphere, difficult tasks, repetitive motion tasks, poor equipment access or egress, exposure to hot surface [ > 140?F], dust hazards, and others.)?
Have adequate provisions been specified for the safe handling and sampling of corrosive, toxic, carcinogenic, teratogenic, or otherwise hazardous materials?
Have personnel safety devices (showers, eye baths, fall prevention, breathing air systems) been specified?
Will all asbestos-containing insulation be removed/repaired in accordance with plant requirements?
Will secondary surfaces (grating, slip protection coatings) be provided where freezing or slippery materials are handled?
Has confined space entry (including electrical equipment) been adequately addressed in this design?
Has the design included adequate walking/working surfaces in accordance with OSHA standards and plant requirements?
Is potable water kept physically separated from process usage?
Noise level monitoring (document)
Exposure monitoring (document)
New substances
Health care
Toxicity data available
Accident treatment plan
Need for change in periodic medical exam
Occupational hygiene
Inventory of possible sources of exposure
Inventory means to restrict exposure
Methods available to monitor exposure
Suitable personal protection equipment available
Hearing Conservation
Noise level monitoring needed/arranged for new operations
Engineering and administrative controls adequate
Permissible exposure limits for chemical substances
Appropriate exposure monitoring and evaluation arranged to determine compliance with applicable PELs
PELs for mixtures applied when two or more hazardous substances present
Engineering and administrative controls adequate
54) Local Exhaust Ventilation Systems
Performance of local exhaust ventilation systems
Local exhaust ventilation systems placed on inspection and maintenance program
55) Control of Potential Mutagens or Carcinogens
Are materials used having control levels A, B, C, or D?
In the plant
In the laboratory
56) Hazard Communication Program
Location inventory of chemicals updated
Hazardous materials identified in accordance with definitions
MSDSs on file and available to all employees
Chemical containers labeled (or alternate means of label information provided)
Piping labeled
Training
57) Respirator Protection
Review/confirm conformance with Corporate Industrial Hygiene Program
Respirator selection in accordance with selection charts and specified in writing
Pressure-demand SCBAs
Emergency “escape only” respirators
User medical clearance
Facial hair policy
Initial issues verified by supervision
Fit testing
Replacement of cartridges and canisters
Inspection and maintenance
Breathing air tested/tagged
Training
Smoking policy established
58) Laboratory Control
Process Laboratory Support Plan communicated
Staffing adequate
Laboratory facilities adequate
General
Emergency exits marked
Emergency lighting
Safety shower & eyewash
Fire protection
Laboratory equipment
Suitable and adequate
Maintenance provisions needed
Storage and handling of chemicals
Reagent storage
Segregation adequate (oxidizers, acids)
Flammable liquid storage
Refrigerator for flammables explosion-proof
Sample storage
Sample and waste disposal
Compressed gases
Cylinder location safe (for example, away from heat sources)
Quantities limited to immediate requirements
Separation of flammable and oxidizers
Toxic gas use limited to small cylinders
Local exhaust ventilation for toxic gases
SCBAs available for toxic gases
Personnel trained in SCBA use as needed
Laboratory procedures
Analytical procedures written and verified
Sampling procedures included
PPE requirements specified
Training completed
Industrial Hygiene
59) Maintenance
Necessary maintenance information in place
Design drawings: for example as-built P&IDs, electrical schematics, isometric piping drawing
Piping specifications
Equipment purchase orders
Equipment manuals
Vendor prints
Initial inspection and test results
Resources adequate
Needs communicated
Plant personnel
Contract maintenance (arrangements completed)
Shop facilities
Specialized requirements
Requirements defined
Skills available
Equipment available
Procedures developed
Training completed
Certificate obtained and documented
Maintenance management
Service contracts arranged
Maintenance management system in place
Spare parts
Requirements defined by Maintenance Department
Procurement complete
Start-up needs on hand
Storage security
Quality assurance program in place for critical equipment
Materials of construction/quality of maintenance materials and parts
Workmanship
Preventive maintenance/mechanical integrity program developed
Machinery
Boilers and pressure vessels
Critical equipment, vessels, piping, check valves, expansion bellows, flexible piping connectors, hoses defined
Critical equipment inspection and test methods and frequencies defined
Conservation vents, flame arrestors, PSEs, PSVs inspection and test methods and frequencies
Critical instruments defined
Proof-testing frequency
Proof-testing procedures, validity
Maintenance of combustion safety controls on direct-fired equipment
Inspection and testing acceptance criteria developed and documented
60) Training
Operations and Maintenance
Initial qualifications of personnel (Knowledge and skills)
Training program content vs. needs
Safety Orientation for new employees
General Safety training
Job-specific training
Basic knowledge and skills
Specialized knowledge and skills
General process knowledge
Material hazards, MSDSs
Process hazards
Process procedures
Operating limits
Consequences of deviations
Responses to deviations/abnormal conditions
Emergency procedures
Field training
Location of:
Emergency equipment, showers, alarms
Fire-fighting equipment
Leak/spill prevention
Reporting, mitigation
Emergency drills
Compliance with OSHA 1910.120 for hazardous waste operations
New emergency response training requirements
Measurement of training
Effectiveness/certification (when applicable)
Formal documentation of training
Team assessment of training effectiveness
61) Commissioning Activities
Commissioning plan and schedule
Detailed, step-by-step plan written
Plan adequately reviewed
Responsibilities clearly defined and understood
Plant verification of any equipment and systems check-out done by contractor
Construction inspection by plant
Confirm line-by-line conformity to P&IDs verified by plant, including:
Materials of construction
Location of instrument elements/connections
Orifice plate specifications and orientation
Ranges of local PIs and TIs
All local TIs have thermowells
Identifies and relief pressure of PSEs & PSVs
Actuated valve failure modes
Equipment internals
62) Vessels and Piping
Stress relieving done and documented as required
Field radiography done and documented as required
Pressure/Leak testing done and documented
Cleaned and flushed (instruments, control valves, check valves protected)
Special commissioning requirements (such as chemical cleaning, passivating, or testing)
Vents and pressure relief valves
Shipping supports removed from conservation vents
Relief pressure of PSVs verified by test
63) Fire Protection Systems
Fire water systems inspection and commissioned
Fire water pump acceptance test(s) completed and witnessed
Other non-water fire protection system acceptance test(s) completed and witnessed (for example, CO2 or dry chemical
New fire protection signaling systems and alarms commissioned
Copies of completed test forms forwarded to insurance carrier and Corporate Risk Department
New fire protection equipment, signaling systems and alarms placed on regular inspection and testing programs
64) Electrical Grounding
Resistance of building and equipment and grounding systems measured <5 ohms
Resistance to ground of all piping sections carrying flammable liquids and combustible powders measured <5 ohms
65) Ventilation Systems
Ventilation systems balanced
Performance of local exhaust ventilation systems checked for conformance
66) Machinery
Alignment checked
Absence of excessive forces on pump casings and other equipment from connected piping
Pre-startup screens installed in pump suctions
Agitator impeller security
Lubrication systems functional
Cooling systems functional
Seal flush systems functional
Rotation checked
Vibration measurements
Performance tests
Other baseline data collection
67) Instruments and Control Systems
Program software checked
Instrument loop sheet index available
Pneumatic lines blown clean
Loop checking done and documented
Instrument calibrations done and documented review methods
Alarm and trip points set and documented
Interlocks tested
Digital control system review and tests
Combustion safety controls on direct-fired equipment
Equipment inspection, adjustment and testing documented
Punch list
Review status
Daily update
Priorities with respect to start-up acceptable
68) Water Batching Trial
Plan developed
69) Start-up Considerations
Start-up plan and schedule
Written and reviewed
Procedures for initial start-up specifically covered in the operating
Instruction manual or under separate cover
Reviewed and approved if separate
Raw materials supply
Technical support
Adequate
Lines and limits of authority clear
Maintenance support
Industrial hygiene monitoring
Equipment monitoring
Performance measurements and tests
70) General Regulatory Compliance
New Substances
Review of toxicity to environment
Persistency in the environment
Prevention of exposure to environment
Destruction of substance when necessary
Toxic Substances Control Act (TSCA)
Project reviewed for any new requirements which might be imposed on the plant location under TSCA
Transportation
New transport operations adequately reviewed for compliance with all applicable DOT (or equivalent) regulations
Emissions
Operating permits obtained as directed by the site or corporate environmental departments
Effluents
New operations covered within the present NPDES permit or a new permit has been obtained
Hazardous wastes
Determined whether particular wastes qualify as hazardous wastes under federal, state and/or local laws and regulations
On-site storage, treatment and/or disposal of hazardous wastes
Reviewed for compliance with applicable laws and regulations, documentation?
Off-site transportation and disposal of hazardous wastes reviewed with waste coordinator, documentation?
PCBs
Review equipment for PCB hazardous properties
71) Supplementary Checklist for New Plant Sites
Plant Security adequate?
Access controlled and adequate?
Fencing in place?
Visitor controls in place?
Vehicle controls in place?
Restrictions posted?
Communications systems in place?
Normal
Emergency back-up
Safety Program up-to-date?
Accountability assigned?
Program conformance with Corporate Safety Standards?
Conformance with group safety standards?
First aid and emergency medical response planned?
Location procedures written?
Training conducted?
Industrial hygiene program in place?
Accountability
Program conformance with Corporate Industrial Hygiene Standards
Fire protection organization established
Location organization established?
Level of protection established in accordance with insurance requirement and Corporate Risk Department
Training conducted in accordance with standard
Equipment provided in accordance with standard
Municipal fire department (or equivalent) trained?
Response time and capabilities consistent with location needs and fire protection organization?
Liaison established
Familiarization
Drills
Process Safety Management (PSM) elements built?
A site PSM coordinator appointed?
PSM Training conducted
72) Administration
Based on the current design, is the proposed change consistent with the original Process Hazard Analysis (PHA) assessment?
Does the design comply with corporate standards?
Has the impact of the change on existing buildings been considered? (That is, the design and location of new or modified equipment near occupied buildings, occupying a previously unoccupied building, and others.)
Has any impact, beyond unit boundaries, associated with this change been properly dealt with and/or communicated?
Have exposures to existing buildings (including pipe racks and cable trays) been considered when siting new vessels, utilities, temporary/permanent buildings or sheds, and others?
Have noncombustible materials or construction been used?
73) Material Safety Regulatory Status
Have the following change scenarios been considered for possible Toxic Substance Control Act (TSCA) applicability?
Previously non-isolated intermediates being temporarily isolated and/or held even for a short time, in non-hard-piped process equipment or in storage vessels (for example, drums).
Previously non-isolated intermediates being held for an extensive period (for example, 24 hours or longer) in hard piped process equipment.
Material previously burned or disposed of as a waste is reprocessed or sold.
Different reactants or catalysts or different feed ratios are being used, thus producing different reaction products for TSCA purposes.
Change in the components or reactants in a polymer from < 2 % to > 2 % of the dry weight of the polymer produced.
The TSCA Inventory status of different catalysts or reactants is unknown. If any of the above change scenarios are about to happen, contact the plant TSCA Coordinator immediately for an in-depth station of TSCA issues. Provide documentation of any concerns and their resolution.
Have Material Safety Data Sheets (MSDS) or Preliminary Product Safety Data Sheets (PPSDS) been obtained for all chemicals to be handled, including isolated intermediates? (Consider changes in minor components of products and by-products)
Has the potential for a hazardous chemical reaction in sumps and sewers been considered?
Have all other potential product regulatory issues been addressed, for example, Department of Transportation (DOT), Federal Insecticide, Fungicide, and Rodenticide Act (FIFRA), Bureau of Alcohol, Tobacco, and Firearms (BATF), Food and Drug Administration (FDA) and ISO 9001?
74) Temperature Control / Reactivity
Has potential for formation of unwanted by-products been adequately addressed?
Has potential for loss of flow or reverse flow been adequately addressed?
Have adequate provisions been made so that normally dilute but reactive materials CANNOT be concentrated or accumulated in unexpected areas (stagnant pipe/valves; utility systems; feed or reaction vessels, sewers, and others.)?
Is adequate freeze protection provided?
75) General Valves and Piping
Have the proper Valve and Piping specifications been used?
Have cross-tied lines (pump headers, utility lines, between high/low pressures, and others.) been reviewed to minimize contamination potential and eliminate mixing of reactive chemicals?
Have test methods and documentation requirements been specified to ensure the integrity of new and revised piping systems?
Will sample points be properly configured for safe sampling of hazardous chemicals?
Have all open ended valves and hand-operated ball valves been designed in accordance with environmental requirements (that is, NESHAPS covered materials such as benzene and formaldehyde) or plant standards?
Have hot-taps been reviewed and eliminated where possible?
Will necessary excess flow and back-flow prevention measures be provided?
Has line expansion and vibration during startup, shutdown, cleaning, normal operation, and others, been considered, and, if appropriate, analyzed in detail?
Has the potential risk and consequences of hydraulic hammering been considered?
Have appropriate materials of construction been considered for compatibility, corrosion resistance and GMP requirements? (Consider 0-rings, gaskets, diaphragms, and others.)
Have the temporary start-up strainers been identified to ensure removal for normal operation?
Has the design included the proper encasing of underground piping at stress points (for example, roadways, railroads, and others.)?
76) Rotating and Mechanical Equipment
Have special precautions for safe operation of equipment been considered? (Reverse flow, minimum flow, maximum head, sudden flow increase during startup, total recycle, vapor locking, volute drainage, Emergency Shutdown Device(s) (ESD), and others.)
Do new and revised pumps and/or pump seals meet and GMP requirements and corporate standards?
Have lubricants and buffer fluids been properly selected to meet any GMP requirements (that is, food grade) such that leakage into the process will not result in undesired chemical reactions or product contamination?
Will moving parts on machinery be properly guarded?
Will pumps be located in accordance with corporate Standards?
Are the emergency shutdown systems (over speed, ground fault, high temperature, vibration, and others.) adequate?
Have appropriate materials of construction been considered for compatibility, corrosion Resistance and GMP requirements? (Consider 0-rings, gaskets, diaphragms, and others.)
Will adequate pressure relief be provided for new or modified pump systems?
77) Instrumentation
Has the potential for instrument failure been adequately addressed?
Have all new shutdown devices been designed to permit testing.
Have potential consequences of instrument or computer failure (redundancy, backup power supply, or others) been considered?
Has control valve fail-safe position on loss of electric power or air/nitrogen been properly specified to minimize the impact of failure?
Have provisions been made to safeguard against risks associated with control valves going full open or closed (mechanical stops, limit switches, and others.)?
If the change affects a shutdown or ESD system, have issues been addressed?
Will the alarms associated with critical instruments be clearly displayed in the control room?
Have any special concerns with regard to response time or sequencing been adequately addressed? (Consider over speed trips, hydraulic hammer, surge control, and others.)
Have process changes (capacity change, density, viscosity, vapor pressure, and others.) been considered in the design of new and existing instrumentation?
Has ESD control logic been reviewed?
Will temperature elements be mounted in thermo wells?
Have appropriate materials of construction been considered for compatibility, corrosion Resistance and any GMP requirements? (Consider 0-rings, gaskets, diaphragms, and others.)
Has adequate local instrumentation been addressed for safety and trouble-shooting purposes?
Is the location of sensing elements proper to ensure that they are actually measuring what you want measured?
78) Fire Protection
Has the potential for static electricity buildup been adequately addressed?
Has proper grounding of all electrical and process equipment (including piping and shipping containers) been specified?
Will fire containment be adequate where hazardous or reactive chemicals are present which can result in high energy release when mixed, contaminated, heated or otherwise mishandled?
Has spontaneous heating of leakage into insulation been adequately considered?
Are provisions made for safe handling of flammable or potentially explosive materials? Consider materials of construction, cleanup and preparation of equipment for maintenance.
Are all fire water spray-system modifications being designed (including flow calculations) and installed by qualified personnel or contractor?
Have modifications or additions to fire protection systems been reviewed or accepted by the Safety Department or property insurance carrier?
Will vents potentially containing flammables be provided with adequate safety equipment (flame arrestors or inert gas purge system)?
Will an adequate detection (vapor or explosive gas detectors) and response system be provided where a vapor cloud is likely?
Have the risks associated with any ignition source or explosive gas mixture been adequately dealt with?
Has adequate fire safety equipment been specified and located where needed?
Has deluge water overflow from containment systems been determined and reviewed properly?
Is diking, curbing, or drainage adequate to contain spills and contaminated rainwater? [Resource Conservation and Recovery Act (RCRA)]
79) Waste Water Treatment and Spill Prevention
Does this design address the potential for spills, releases, compatibility and flammability?
Has the Environmental Health and Safety Department (EHS) been notified of any new waste stream sources or increased quantities from existing sources?
Has EHS evaluated waste streams for impact on Plant Waste Water Treatment Facilities? (Compatibility with existing plant waste treatment system capabilities, required provisions for RCRA hazardous waste chemicals, proper notification of governmental agencies, effect on EHS operations personnel, effect on discharges to the Publicly Owned Treatment Work(s) (POTW) or river, and others.)
Will diking, draining, curbing, and special protective surface coatings be adequate to contain leaks and the worst case spill scenario?
80) Solid and Liquid Waste
Has at-source waste minimization been adequately addressed?
Have adequate provisions been made for disposal of all wastes (including drums, bags, filter elements, liquid residues, asbestos-containing insulation, PCBs, contaminated soil, demolition rubble and processing equipment)?
Have waste streams intended for disposal in the boilers been reviewed by the EHS Department?
Have the following change scenarios been considered for possible RCRA applicability?
Creation of a new hazardous waste.
Change in composition of an existing hazardous waste.
Modifications of a facility in hazardous or solid waste service. If any of the above change scenarios are about to happen, contact the plant EHS Department immediately for an in-depth examination of RCRA issues. Provide documentation of any concerns and their resolution.
81) Air Emissions
Have the following change scenarios been considered for possible Air Emission applicability?
Increase in potential emissions of volatile organic compound
New emissions of hazardous air pollutants
Increase in potential emissions of hazardous air pollutants
Change of service for equipment
Composition change in existing emissions
Addition of new emission points (including fugitive sources such as valves and relief devices) or physical change in existing emission points or monitored points. If any of the above change scenarios are about to happen, contact the plant EHS Department immediately for an in-depth examination of permit issues. Provide documentation of any concerns and their resolution.
Have any increases in air emissions of flammable, toxic, corrosive, reactive or otherwise hazardous chemicals been identified, quantified and communicated to the plant EHS Department (to obtain necessary permitting, identify control devices being used, and others.)?
Has the change been reviewed to determine if it is subject to any requirements to recalculate Toxic Release Inventory (TRI), re-evaluate control device efficiency, or otherwise manage the change under state or federal requirements?
82) Process Equipment
Has a pressure vessel engineer reviewed the design/repair specifications and considerations for new, altered or repaired equipment?
Have the appropriate welding procedure(s) been identified?
Has spare equipment been provided where needed for safety?
Have appropriate materials of construction been considered for compatibility, corrosion resistance and any GMP requirements? (Consider 0-rings, gaskets, diaphragms, and others.)
Has the documentation for piping and equipment been appropriately updated?
83) Computer Software and Systems
Are adequate safeguards in place to ensure the process is controlled within the safe operating envelope?
Is the fail safe condition of controllers adequate?
84) Overall Safety Considerations
Will adequate design provisions exist for cleanup and preparation of equipment for maintenance of equipment/piping/control systems (including lockout of all energy sources and double isolation where required)?
Have the consequences of loss of any utility been adequately addressed?
Has cathodic protection, electrical continuity and electronic grounding been adequately addressed?
Has necessary structural analysis been performed?
Will adequate provisions be made to ensure equipment idled by this change is maintained in a safe condition?
Has a change in utility consumption been properly communicated?
Has the design included the need for labeling including equipment apparatus numbers, identity, content, direction of flow, and others?
Has the design included requirements for adequate area lighting?
Has the design of the equipment included adequate room and clearance for proper maintenance?